## Slide 1: Field tests of Individual Blade Control and its impact on the wind turbine components lifetime
Carlos Gonzalez
29 September

## Slide 2
Engineering organisation providing advanced control solutions to wind and tidal turbines.
Part of SgurrEnergy
Global leader in software, analysis and services for gearbox, bearings and driveline systems.
Project partly funded by DECC

## Slide 3: Why Individual Blade Control?
IBC extends life of blades and drive train components
IBC reduces CAPEX and OPEX costs
Turbulence
Low Level Jets
strong shear
veer
Coherent eddy
Wind shear
Yaw misalignment
Tower
shadow
IBC
Notes: The underlying cause of most loads on the wind turbine is the wind itself. What we find though, is that with non-uniform wind fields, the damage to the turbine is greater. Turbulence, wind shear, low level jets, veer, yaw misalignment, coherent eddies, tower shadow all negatively impact on the turbine loads. In particular at harmonics of the rotational frequency of the turbine. This is due to rotational sampling of the wind field.
So taking wind shear as an example, during each rotation the blades experience high wind speeds at the top of their rotation, and low wind speeds at the bottom of their rotation, and this loading repeats itself once per revolution. Or if we consider a coherent eddy passing through, each rotation the blade is going to slice through that eddy, experiencing a change in loading that repeats once per revolution. On many wind turbines, there are three blades, this means that for other components, for example the drivetrain, rather than experiencing a once per revolution loading, they experience this as a 3 times per revolution loading, as each blade contributes to the loading on the main shaft. Other harmonics may also manifest themselves, depending on the symmetries in the wind field.

## Slide 4: IBC control structure
IBC
Central
Controller
Wind
Turbine
b1
b2
b3
M1
M2
M3
Rotor speed
Reference speed
Blade controller
Blade controller
Blade controller
Collective pitch demand
Individual pitch demands (, , )
Blade moments (M1 , M2 , M3)
Hub accelerations
Notes: To pitch the blades individually, we have a control structure looks something like this
What each term is

## Slide 5: Implementation on Clipper C96
Bending Moments and
Hub Accelerations
IBC Hardware
Pitch Control Unit
Turbine Control Unit
Individual Pitch Angles
Collective Pitch
Pitch Feedback
Pitch
feedback
Turbine Control Unit
Pitch Control Unit
Collective pitch angle
Pitch feedback
Clipper C96 2.5MW wind turbine owned by University of Minnesota

## Slide 6: Field data - Results
10 % Fatigue blade loads reduction (out-plane bending moment)
Notes: After running with the two methods we can answer the question, is AT working? The answer is yes. We can affirm that by looking how AT reduces the fatigue loads on the blade. The blade loads has been reduced at the 1P frequency as intended. ATLAS wasn’t designed to reduce the whole 1P peak. The graph on the right show the fatigue reduction when we aggregate lots of data under different conditions (wind speed, TI). Every point represents the equivalent fatigue load for 10 minutes of data captured and the lines are the average of these points at different wind speeds. The reduction with AT is around a 10 %

## Slide 7: Field data - Results
ATLAS does not interfere with the speed/power control
Same power curve
Power curve
Generator speed
spectrum
Notes: The other aspect to verify is that is the new controller does not interfere with the speed and power control.
The graph on the right depicts part of the power curve. Every point is the average power for 10 minutes of data and the lines are the mean value binned respect to wind speed. As you can see there is not a significant variation between both power curves so the same energy is captured with and without ATLAS. The 2nd graph shows the PSD of the generator speed. For those who are not familiar with the representation on the frequency domain, it is not that important, the important part is that both lines match really well.
As a conclusion we can say that AT does not have any impact on the wind turbine controller and is effective on reducing loads.

## Slide 8: IBC design validation
Wind conditions:
Wind speed
Turbulence intensity
Wind shear
Air density
?
Loads, generator speed, pitch angle …
Notes: The 2nd objective of the demonstration is to validate that the model and design methods match to what is observed in reality. On site we had a very well instrumented met mast with anemometers and wind vanes at different heights including the hub and top and bottom tip heights.
We recorded a lot of information from the wind turbine, here are the example of some of the signals that we recorded. For example blabla. From the met mast we obtained the wind and meteorological conditions that can input our model and the question is: is the output of the model the same as we observed in reality?

## Slide 9: Model Validation: real vs simulated
Flapwise bending moment
Generator speed (Collective)
a) Collective
b) IBC

## Slide 10: Benefits - Drive train analysis
RomaxWIND model of drive train
Assess Lifetime with ISO 6336 and ISO 281:1990
Romax bespoke calculation methods

## Slide 11: Drive train benefits
Gearbox (Minimum safety factors for gears)
Main Bearing Damage (%)
Reduces peak stresses: It can prevent other failure modes seen in the field: edge load failure, cage failure and cage debris related failures
Control strategy | 2.5 MW | 2.3 MW
Collective | 0.95 | 0.98
IBC | 1.05 | 1.12
Control strategy | Upwind bearing |  | Downwind bearing | 
 | 2.5 MW | 2.3 MW | 2.5 MW | 2.3 MW
Collective | 89.9 | 81 | 59.1 | 49.1
IBC | 77.3 | 65 | 58.7 | 40.6
15 % average damage reduction
10-15 % improve

## Slide 12: Impact on pitch bearing
NREL DG03 method used
  Little difference on life between the IBC and collective control
  Majority of the oscillations are below the dither amplitude (0.17°) and a slight increase in the overall number of oscillations
Lower peak loading for the IBC case  This should provide fatigue benefits
Romax analysis concluded that the pitch bearing is not affected by the IBC strategy.

## Slide 13: Conclusions
IBC demonstrated on a real wind turbine
  Easy to retrofit and integrate into new wind turbines
Design methods and performance validated from field data
Target 10 % blade loads reduction achieved
Extend the life of the gearbox. Safety Factors improved by 18 %
Main bearing raceway damage reduced by 15 %
No impact on the pitch bearing life.