## Slide 1: MODELLING THE FAILURE BEHAVIOUR OF WIND TURBINES
Dipl.-Ing. M.Sc. Stefan Faulstich, Volker Berkhout, Jochen Mayer, David Siebenlist Fraunhofer Institute for Wind Energy and Energy System Technology

## Slide 2: Motivation
  O&M costs are to be lowered constantly
  MAS-ZIH – Multi-Agent Simulation as Decision Support for a reliability-based Maintenance (zuverlässigkeitsorientierte Instandhaltung)
  Large uncertainty on the demand side, which is the characteristics of failure behaviour of wind turbines

## Slide 3
Implement reliability module in simulation tool
Simulation of failure behaviour
Framework
Failure statistics
Function per failure category & per component
Simulation
Identify lifetime describing variable
Estimate parameters for reliability functions
Reliability characteristics
Assignment to failure categories
Wind turbine structure
Failure categories
Approach

## Slide 4
Wind turbine structure
Failure categories
Framework

## Slide 5
i | Failure category | Share of total failures (%)
1 | Random | 15%
2 | Early | 5%
3 | Aging | 15%
4 | Fatigue | 55%
5 | Overload | 10%
Failure statistics
Reliability characteristics
Assignment to failure categories
Average Rotor Blade Failure Rate:
/(Turbine * year)
1. Determine the total number of failures for the simulation period
2. Weighting of failure categories

## Slide 6
Function per failure category & per component
Identify lifetime describing variable
Estimate parameters for reliability functions
=
3. Functions of time-dependent failures

## Slide 7
Identify lifetime describing variable
Estimate parameters for reliability functions
=
Wind speed [m/s]
4. Function of fatigue failures
5. Function of overload failures
Function per failure category & per component
6. Component specific failures
Notes: Lebensdauermerkmal, produzierte Energie bzw. Volllaststunden
Steigende Ausfallrate, Formfaktor β = 2,2
Erwartungswert für 4MW Anlage ca.130GWh
η = 160GWh

## Slide 8
Implement reliability module in simulation tool
Simulation of failure behaviour
λ(t)
λ(E)
λ(v)
Simulation

## Slide 9
Implement reliability module in simulation tool
Simulation of failure behaviour
Simulation

## Slide 10
Implement reliability module in simulation tool
Simulation of failure behaviour
Simulation

## Slide 11
Conclusion
  Modelling the failure behaviour of wind turbines is an essential part of offshore simulation software
  failure model based on a reliability-block-diagram has been proposed
  incorporates different failure categories
  essential for better including preventive maintenance strategies
  include increased failure rates at higher wind speed and seasonal effects on failures due to lightning or icing

## Slide 12: Thank you for the attention
Dipl.-Ing M. Sc. Stefan Faulstich
Reliability & Maintenance strategies
R&D Division Energy Economy and Grid Operation
Fraunhofer Institute for Wind Energy and
Energy System Technology IWES
Königstor 59 │ 34119 Kassel
Telefon: +49 (0)561-7294 253
E-Mail: stefan.faulstich@iwes.fraunhofer.de
© alpha ventus picture library