## Slide 1: Frequency Converters in Wind
Stephan Ebner, John Eckerle | ABB Switzerland Ltd | WindEurope Summit 2016 | 27-09-2016
A technical Boon or Bane?

## Slide 2: Frequ.-Converters in Wind. A technical Boon or Bane?
  Retrospection to turbines without frequency converters
  Improvements to wind turbines using frequency converters
  Today’s „must have“ features of wind turbine frequency converters
  Additional operation modes of a wind turbine frequency converter
  New features of frequency converters in the benefit for the wind turbine and the wind park
  Benefits of medium-voltage converters for large offshore turbines
Contents of this Presentation

## Slide 3: Frequ.-Converters in Wind. A technical Boon or Bane?
Large power plants utilizing large turbines with large fix speed static-excited synchronous generators Three Gorges Dam in China utilizing 32 turbine sets of 700 MW
Fix speed possible (no converter) because controlled stable primary power flow (steam, gas, water head), often in combination with mechanical turbine features (e.g. guide vane)
Powerfactor/voltage control by excitation
Stable operation, LVRT by mass inertia for easy grid stabilization
Highly reliable and efficient
Traditional Power Generation
Nobody is thinking of using a frequency converter in traditional power generation. Having a constant primary energy feed (steam, gas, water) a constant power generation is possible. Generators are DirectOnLine, synchronized with the grid.

## Slide 4: Frequ.-Converters in Wind. A technical Boon or Bane?
Positive aspects of power generation w/o frequency converters
Aspect | Status | Reason
Complexity of power generation | Low | No converter, no converter control
CAPEX / OPEX cost | Low | No purchasing and maintenance cost of converter
Availability | Good | No converter = no converter failures
Losses in drivetrain | Low | No converter = no converter losses
Creation of harmonics | Low | No converter = no harmonics creation
Traditional power generation reach good LCOE levels and grid code compliance without utilizing frequency converters.
Notes: - also space for installtion is required
vice versa: … have to deal with all this topics, that we touch throughout this presentation

## Slide 5: Frequ.-Converters in Wind. A technical Boon or Bane?
History of Wind Turbines and use of frequency converters
Fix Speed Turbines
Fix two Speed Turbines
DFIG Turbines ±30% Var.-Speed
Var.-Speed Turbines Full Converter Low-Voltage
Fix Speed Turbines with resistor
Var.-Speed Turbines Full Converter Medium-Voltage
Hydraulic Gear Box Var.-Speed
No Converter
OptiSlip Turbines <20% Var.-Speed
1980’s
1980’s
1980’s-1990’s
1980’s-1990’s
1990’s
2000’s
2010’s

## Slide 6: Frequ.-Converters in Wind. A technical Boon or Bane?
History of Wind Turbines and use of frequency converters
Fix Speed Turbines
Fix two Speed Turbines
DFIG Turbines ±30% Var.-Speed
Var.-Speed Turbines Full Converter Low-Voltage
Fix Speed Turbines with resistor
Var.-Speed Turbines Full Converter Medium-Voltage
Hydraulic Gear Box Var.-Speed
No Converter
OptiSlip Turbines <20% Var.-Speed
1980’s
1980’s
1980’s-1990’s
1980’s-1990’s
1990’s
2000’s
2010’s
Notes: First generations of wind turbines have been built w/o frequency converters, realizing that improvements are needed to improve the performance
The hydraulic gear box type turbine used rarely

## Slide 7: Frequ.-Converters in Wind. A technical Boon or Bane?
Negative aspects of turbines w/o frequency converters
Aspect | Status | Reason
Wind turbine yield | Highly improvable | Rarely matching wind-speed/ blade-speed optimum ratio.
Stability in power generation | Critical | Stability at high wind was challenging.
Handling of grid disturbances | Critical | Grid disturbances easily trips the turbine.
Grid support with reactive power | Very limited | Voltage stabilization is not possible.
Decoupling of mech. drivetrain vs. electrical grid | No | Mechanical oscillations hit the grid and vs. grid disturbances hit the mechanics.
Operation of other drivetrain concepts than asynchronous high speed generator | No | Generator frequency must match with grid frequency. Generator is typically a high speed induction generator.
The wind turbines of the 1980/90´s without frequency converters have been facing various drawbacks and limitations. Wind power LCOE far off the traditional power generation.

## Slide 8: Frequ.-Converters in Wind. A technical Boon or Bane?
With DFIG wind turbines frequency converters got required
Fix Speed Turbines
Fix two Speed Turbines
DFIG Turbines ±30% Var.-Speed
Var.-Speed Turbines Full Converter Low-Voltage
Fix Speed Turbines with resistor
OptiSlip Turbines <20% Var-Speed
Var.-Speed Turbines Full Converter Medium-Voltage
Hydraulic Gear Box Var.-Speed
DFIG Converter
1980’s
1980’s
1980’s-1990’s
1980’s-1990’s
1990’s
2000’s
2010’s
Notes: A nice improvement by the DFIG type turbine
The converter is sitting in the generator rotor feedback path connected by slip rings, the generator stator is still hard conected to the grid
The converter power is only a fraction of the turbine power, for ±30% Var-speed about 30% of the turbine power, example 3MW turbine = 1MW converter

## Slide 9: Frequ.-Converters in Wind. A technical Boon or Bane?
Aspects of turbines with DFIG converter
Aspect | Status | Reason
Wind turbine yield | Okay | Matching wind speed / blade speed optimum ratio at ±30% of nominal speed.
Stability in power generation | Fair | Power stability at turbine nominal rating is given
Handling of grid disturbances | Okay | Grid disturbances can endanger a turbine trip. Additional crowbar is required.
Grid support with reactive power | Okay | Voltage stabilization is possible within limited converter capability.
Decoupling of mech. drivetrain vs. electrical grid | Okay | Grid disturbances hit mechanic parts.
Operation of other drivetrain concepts than high speed induction generator | No | Drive train concept is «per-se» an asynchronous high speed induction generator.
CAPEX / losses / space / harmonics | to deal with | General drawbacks of using converters are valid.
The DFIG wind turbine achieved a significant step for a better LCOE of wind power. Several drawback and limitation remain and potential for improvement remains.

## Slide 10: Frequ.-Converters in Wind. A technical Boon or Bane?
Full power converters open up new possibilities in turbine design
Fix Speed Turbines
Fix two Speed Turbines
DFIG Turbines ±30% Var.-Speed
Var.-Speed Turbines Full Converter Low-Voltage
Fix Speed Turbines with resistor
OptiSlip Turbines <20% Var-Speed
Var.-Speed Turbines Full Converter Medium-Voltage
Hydraulic Gear Box Var.-Speed
Full Converter
1980’s
1980’s
1980’s-1990’s
1980’s-1990’s
1990’s
2000’s
2005´s
Notes: The converter is sitting in the main power path of the turbine

## Slide 11: Frequ.-Converters in Wind. A technical Boon or Bane?
Aspects of turbines with a full converter
Aspect | Status | Reason
Wind turbine yield | Good | Matching wind speed/ blade speed optimum ratio at full range
Stability in power generation | Good | Power stability at full turbine range rating is given.
Handling of grid disturbances | Good | Converter behavior is adjustable (mainly by SW parameters).
Grid support with reactive power | Good | Voltage stabilization is possible within converter capability.
Decoupling of mech. drivetrain vs. electrical grid | Good | Full decoupling of mechanical drivetrain and grid.
Operation of other drivetrain concepts | Yes | Low-speed (direct drive) and mid-speed generators, also with synchronous generators (e.g. PMG) gets possible.
CAPEX / losses / space / harmonics | to deal with | General drawbacks of using converters are valid
Further important improvements are achieved by using the full power converter. Various new drivetrain designs became possible, e.g. the use of efficient permanent magnet generators and the full utilization of the turbine speed range to further reduce the LCOE of wind power.

## Slide 12: Frequ.-Converters in Wind. A technical Boon or Bane?
A frequency converters is a key component in each wind turbine
Full Converter
DFIG Converter
No Converter
The wind turbines of the 1980/90´s without frequency converters have been facing various drawbacks and limitations. Wind power LCOE far off the classical power generation.
The DFIG wind turbine achieved a significant step for a better LCOE of wind power. Several drawback and limitation remain and still have potential for improvement.
Further important improvements are achieved by using the full power converter. Various new drivetrain designs became possible, e.g. the use of efficient permanent magnet generators and the full utilization of the turbine speed range to further reduce the LCOE of wind power.
The performance and the achieved LCOE level of present wind turbines only becomes possible by using frequency converters.

## Slide 13: Frequ.-Converters in Wind. A technical Boon or Bane?
Stable Grid Operation Grid Stabilization Grid Code Compliant
  Reactive Power Supply
Drivetrain Decoupling Generator / Grid
No load chages at LVRT Brake Resistor power burn
Various Drivetrain Concepts possible
Perm. Magnet Generator
Low-Speed (Direct) Drive Medium-Speed Drive
Full Power Curve Utilization
Fully Var.-Speed 0-100% Increased Turbine Yield
Standard Features of a Full Converter Drivetrain Design
September 27, 2016
WindEurope Summit 2016 | Hamburg
Notes: Going into the key features of a full-power converter (low-voltage or medium voltage)

## Slide 14: Frequ.-Converters in Wind. A technical Boon or Bane?
Stable Grid Operation Grid Stabilization Grid Code Compliant
  Reactive Power Supply
Drivetrain Decoupling Generator / Grid
No load chages at LVRT Brake Resistor power burn
Various Drivetrain Concepts possible
Perm. Magnet Generator
Low-Speed (Direct) Drive Medium-Speed Drive
Standard Features of a Full Converter Drivetrain Design
September 27, 2016
WindEurope Summit 2016 | Hamburg
Full Power Curve Utilization
Fully Var.-Speed 0-100% Increased Turbine Yield

## Slide 15: Frequ.-Converters in Wind. A technical Boon or Bane?
Stable Grid Operation Grid Stabilization Grid Code Compliant
  Reactive Power Supply
Various Drivetrain Concepts possible
Perm. Magnet Generator
Low-Speed (Direct) Drive Medium-Speed Drive
Standard Features of a Full Converter Drivetrain Design
September 27, 2016
WindEurope Summit 2016 | Hamburg
Full Power Curve Utilization
Fully Var.-Speed 0-100% Increased Turbine Yield
Drivetrain Decoupling Generator / Grid
No load changes at LVRT Brake Resistor power burn
Notes: The DC-Link in the converter (see picture: one side generator/other side step-up transformer) is decoupling the mechanical and the electrical side
A constant generator torque set point is applied by the gen.-side converter
A brake chopper and a brake resistor is connected to the DC-link
A rating of the brake resistor shall pick up the active power of two consequent LVRTs (about 6 sec), if designed too small then the generator torque is released that could result in a turbine over speed

## Slide 16: Frequ.-Converters in Wind. A technical Boon or Bane?
Stable Grid Operation Grid Stabilization Grid Code Compliant
  Reactive Power Supply
Standard Features of a Full Converter Drivetrain Design
September 27, 2016
WindEurope Summit 2016 | Hamburg
Full Power Curve Utilization
Fully Var.-Speed 0-100% Increased Turbine Yield
Drivetrain Decoupling Generator / Grid
No load chages at LVRT Brake Resistor power burn
Various Drivetrain Concepts possible
Perm. Magnet Generator
Low-Speed (Direct) Drive Medium-Speed Drive
Notes: DFIG was only possible with asynchronous generators (high speed), now many more concepts are possible
Permanent magnet generators increase the turbine efficiency
The low-speed (direct) drive eliminates the gear box. Also low electrical frequencies must be considered in converter design, in general possible down to 5Hz

## Slide 17: Frequ.-Converters in Wind. A technical Boon or Bane?
Standard Features of a Full Converter Drivetrain Design
September 27, 2016
WindEurope Summit 2016 | Hamburg
Full Power Curve Utilization
Fully Var.-Speed 0-100% Increased Turbine Yield
Drivetrain Decoupling Generator / Grid
No load chages at LVRT Brake Resistor power burn
Various Drivetrain Concepts possible
Perm. Magnet Generator
Low-Speed (Direct) Drive Medium-Speed Drive
Stable Grid Operation Grid Stabilization Grid Code Compliant
Reactive Power Supply
Notes: Full power converters allow full grid control

## Slide 18: Frequ.-Converters in Wind. A technical Boon or Bane?
Production Mode
  Opt. Generator Operation
  Grid code compliance
  Active drive train damping
  Grid resonance prevention
Motor Mode
Rotor Positioning
Drivetrain Hall Test
Back-to-Back Test
StatCOM Mode
Standby Grid Stabilization
Grid Loss Mode
Island Operation
Self-supply of aux. power
Operation modes of a state-of-the-art full converter
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 19: Frequ.-Converters in Wind. A technical Boon or Bane?
StatCOM Mode
Standby Grid Stabilization
Operation modes of a state-of-the-art full converter
Grid Loss Mode
Island Operation
Self-supply of aux. power
Motor Mode
Rotor Positioning
Drivetrain Hall Test
Back-to-Back Test
Production Mode
  Opt. Generator Operation
  Grid code compliance
  Active drive train damping
  Grid resonance prevention
September 27, 2016
WindEurope Summit 2016 | Hamburg
Notes: Production Mode is the normal operation mode of a converter
Active drive train damping is a converter feature that can be switched if desired to stabililize low-frequency mechanial resonances of the wind turbine

## Slide 20: Frequ.-Converters in Wind. A technical Boon or Bane?
Production Mode
  Opt. Generator Operation
  Grid code compliance
  Active drive train damping
  Grid resonance prevention
StatCOM Mode
Standby Grid Stabilization
Operation modes of a state-of-the-art full converter
Grid Loss Mode
Island Operation
Self-supply of aux. power
Motor Mode
Rotor Positioning
Drivetrain Hall Test
Back-to-Back Test
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 21: Frequ.-Converters in Wind. A technical Boon or Bane?
Using the wind turbine converter for test purpose One converter drives generator as a motor - a second converter generates the power back to the grid
  Used for design verification of generator (temp.-rise, efficiency, harmonics, vibration, …)
  Used for wind turbine routine test at production
Use the Converter in Motor Mode for Back-to-Back testing
G
M
WindEurope Summit 2016 | Hamburg

## Slide 22: Frequ.-Converters in Wind. A technical Boon or Bane?
Operation modes of a state-of-the-art full converter
Grid Loss Mode
Island Operation
Self-supply of aux. power
Motor Mode
Rotor Positioning
Drivetrain Hall Test
Back-to-Back Test
Production Mode
  Opt. Generator Operation
  Grid code compliance
  Active drive train damping
  Grid resonance prevention
StatCOM Mode
Standby Grid Stabilization
September 27, 2016
WindEurope Summit 2016 | Hamburg
Notes: Volatge stabilization (Supress voltage or support voltage by acting as STATCOM device)  Phase Shift

## Slide 23: Frequ.-Converters in Wind. A technical Boon or Bane?
Production Mode
  Opt. Generator Operation
  Grid code compliance
  Active drive train damping
  Grid resonance prevention
Motor Mode
Rotor Positioning
Drivetrain Hall Test
Back-to-Back Test
StatCOM Mode
Standby Grid Stabilization
Operation modes of a state-of-the-art full converter
Grid Loss Mode
Island Operation
Self-supply of aux. power
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 24: Frequ.-Converters in Wind. A technical Boon or Bane?
Grid Loss System. How does the Island Mode work?
UPS required for start of Island Mode
Pitch Control sets rotor speed.
Converter generates as much power as needed (Island Mode).
UPS will be recharged by the wind turbine.
UPS feeds auxiliary power in case of calm wind
Main and auxiliary circuit breaker are closed during Island Mode operation
The converter creates auxiliary power directly from the wind turbine generator w/o the need for an extra diesel generator. Wind power reputation as “Green Power remains Green”
Missing grid connection leave installed wind turbines without auxiliary power supply | w/o Island Mode: diesel generators provide auxiliary power but high CAPEX and OPEX
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 25: Frequ.-Converters in Wind. A technical Boon or Bane?
Active Drivetrain Damping Counter Torque Injection
Vibration Damping
Mech. Stress Reduction
Internal or ext. Control
Optimized Pulse Pattern Effective Filtering
Free Harmonic Location
Clear Resonance Areas
Filterless Design Avoiding Grid Resonances
Eliminating Filter Losses
Reducing Footprint Space
Resonance Prevention Passive Harm. Behavior
No Resonance Amplif.
Additional features of a state-of-the-art full converter
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 26: Frequ.-Converters in Wind. A technical Boon or Bane?
Optimized Pulse Pattern Effective Filtering
Free Harmonic Location
Clear Resonance Areas
Filterless Design Avoiding Grid Resonances
Eliminating Filter Losses
Reducing Footprint Space
Resonance Prevention Passive Harm. Behavior
No Resonance Amplif.
Additional features of a state-of-the-art full converter
Active Drivetrain Damping Counter Torque Injection
Vibration Damping
Mech. Stress Reduction
Internal or ext. Control
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 27: Frequ.-Converters in Wind. A technical Boon or Bane?
Active drive train damping reduces turbine stress
T_Ref = torque reference
w_act = actual generator speed
Turbines without drive train damping
  When operating the converter with a constant torque reference several wind turbines components may add oscillations to the drive train which are observable in the generator speed.
Turbine with active drive train damping
  The active damping is done by adding a damping torque to the generators reference torque. Consequently the generator speed gets stabilized. The damping itself then is done by the specific current controller in the closed loop converter control.
The active drive train damping reduces stress on mechanical drive train and therefore increase turbines reliability
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 28: Frequ.-Converters in Wind. A technical Boon or Bane?
Filterless Design Avoiding Grid Resonances
Eliminating Filter Losses
Reducing Footprint Space
Resonance Prevention Passive Harm. Behavior
No Resonance Amplif.
Additional features of a state-of-the-art full converter
Active Drivetrain Damping Counter Torque Injection
Vibration Damping
Mech. Stress Reduction
Internal or ext. Control
Optimized Pulse Pattern Effective Filtering
Free Harmonic Location
Clear Resonance Areas
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 29: Frequ.-Converters in Wind. A technical Boon or Bane?
Power converters create harmonics into the grid.
  Turbine Converter (+HVDC)
Cables, transformers and filter banks introduce resonance poles into the collection grid.
OPP Control adapts harmonics to grid impedance situation
OPP and resonance prevention mitigate the risk of harmonic amplification in the collection grid
September 27, 2016
WindEurope Summit 2016 | Hamburg
Notes: Passives Verhalten: im Text erwähnen

## Slide 30: Frequ.-Converters in Wind. A technical Boon or Bane?
Resonance Prevention Passive Harm. Behavior
No Resonance Amplif.
Additional features of a state-of-the-art full converter
Active Drivetrain Damping Counter Torque Injection
Vibration Damping
mech. Stress Reduction
Internal or ext. Control
Optimized Pulse Pattern Effective Filtering
Free Harmonic Location
Clear Resonance Areas
Filterless Design Avoiding Grid Resonances
Eliminating Filter Losses
Reducing Footprint Space
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 31: Frequ.-Converters in Wind. A technical Boon or Bane?
Filterless Design Avoiding Grid Resonances
Eliminating Filter Losses
Reducing Footprint Space
Additional features of a state-of-the-art full converter
Active Drivetrain Damping Counter Torque Injection
Vibration Damping
Mech. Stress Reduction
Internal or ext. Control
Optimized Pulse Pattern Effective Filtering
Free Harmonic Location
Clear Resonance Areas
Resonance Prevention Passive Harm. Behavior
No Resonance Amplif.
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 32: Frequ.-Converters in Wind. A technical Boon or Bane?
History of Wind Turbines and use of frequency converters
Fix Speed Turbines
Fix two Speed Turbines
DFIG Turbines ±30% Var.-Speed
Var.-Speed Turbines Full Converter Low-Voltage
Fix Speed Turbines with resistor
OptiSlip Turbines <20% Var-Speed
Var.-Speed Turbines Full Converter Medium-Voltage
Hydraulic Gear Box Var.-Speed
Full Converter
1980’s
1980’s
1980’s-1990’s
1980’s-1990’s
1990’s
2000’s
2005´s

## Slide 33: Frequ.-Converters in Wind. A technical Boon or Bane?
Availability Low Part Count
Fuseless Design
High MTBF
Less Maintenance
Size High Power Density
Small Footprint
Tower Location
Efficiency Efficient Semiconductors
Filterless Design
Low Cable Losses
Cabling
Small Currents
Savings on Cabling
Easy Tower Installation
Further benefits using the medium-voltage drivetrain technology
WindEurope Summit 2016 | Hamburg

## Slide 34: Frequ.-Converters in Wind. A technical Boon or Bane?
Size High Power Density
Small Footprint
Tower Location
Efficiency Efficient Semiconductors
Filterless Design
Low Cable Losses
Cabling
Small Currents
Savings on Cabling
Easy Tower Installation
Further benefits using the medium-voltage drivetrain technology
Availability Low Part Count
Fuseless Design
High MTBF
Less Maintenance
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 35: Frequ.-Converters in Wind. A technical Boon or Bane?
Efficiency Efficient Semiconductors
Filterless Design
Low Cable Losses
Cabling
Small Currents
Savings on Cabling
Easy Tower Installation
Further benefits using the medium-voltage drivetrain technology
Availability Low Part Count
Fuseless Design
High MTBF
Less Maintenance
Size High Power Density
Small Footprint
Tower Location
WindEurope Summit 2016 | Hamburg

## Slide 36: Frequ.-Converters in Wind. A technical Boon or Bane?
Cabling
Small Currents
Savings on Cabling
Easy Tower Installation
Further benefits using the medium-voltage drivetrain technology
Availability Low Part Count
Fuseless Design
High MTBF
Less Maintenance
Size High Power Density
Small Footprint
Tower Location
Efficiency Efficient Semiconductors
Filterless Design
Low Cable Losses
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 37: Frequ.-Converters in Wind. A technical Boon or Bane?
Further benefits using the medium-voltage drivetrain technology
Availability Low Part Count
Fuseless Design
High MTBF
Less Maintenance
Size High Power Density
Small Footprint
Tower Location
Efficiency Efficient Semiconductors
Filterless Design
Low Cable Losses
Cabling
Small Currents
Savings on Cabling
Easy Tower Installation
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 38
 | 4MW1 | 5MW2 | 6MW2 | 7MW2 | 8MW2 | 10MW2 | 12MW2
Energy production MV drivetrain to grid [GWh/y] | 18.3 | 23.0 | 27.6 | 32.2 | 37.6 | 46.0 | 55.2
Discounted LCOE using MV drivetrain [€ct/kWh] 3 | 15.2 | 14.7 | 14.1 | 13.5 | 12.7 | 12.1 | 11.8
Using a medium-voltage drivetrain technology cause a substantial lowering of LCOE in large scale offshore wind power generator
1) 3L/4.1kV converter with med.-speed PMG; 2) 3L/3.3kV converter with med.-speed PMG ; 3) Based on German FIT
Result of ABB’s drivetrain study: MV drivetrains provide more energy to grid and lowering LCOE
Frequ.-Converters in Wind. A technical Boon or Bane?
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 39
Generators
Transformers
Converters
Generators
PLC
Motors
Switchgears
Communication
Solutions, wind
power plant control
HVDC Light
HVDC cables
Substation for onshore wind power plants
Offshore HVDC converter station
Offshore AC substation
Collection grid products
HVAC cables
Control and network
management: SCADA,
EMS, GMS
HVDC cables
Asset management
Substation automation and power quality optimization solutions
EMS: Energy Management System
GMS: Generation Mangement System
HVAC: High-voltage Alternating Current
ABB deliveries from A to Z into the wind industry
Frequ.-Converters in Wind. A technical Boon or Bane?
HVDC: High-voltage Direct Current
PLC: Programmable Logic Controller
SCADA: Supervisory Control And Data Acquisition
September 27, 2016
WindEurope Summit 2016 | Hamburg

## Slide 40
Frequ.-Converters in Wind. A technical Boon or Bane?
September 27, 2016
WindEurope Summit 2016 | Hamburg
Thank you !!
Stephan Ebner and John Eckerle
ABB Switzerland
5300 Turgi
stephan.ebner@ch.abb.com john.eckerle@ch.abb.com