## Slide 1: High Definition MMC for platform-less HVDC offshore wind power collection system
Paul McKeever
Head of Research and Development
27 Sept 2016

## Slide 2: Content
Platform-less Offshore HVDC System
  AC vs DC
  Research History
  Current Status
HD-MMC
  State of the art
  HD Proposed Solution
Conclusions/Next Steps

## Slide 3: AC vs. DC Transmission
Wind industry moving further offshore
HVDC more cost effective over long distances
Large wind farms increasingly looking to HVDC for exporting power
Current HVDC converters not optimised for offshore environment
  High capital cost ≈ 16 - 22 % of wind farm
  Low redundancy
Notes: Graph source – National Grid 10-year statement and typical offshore wind farm costs for AC/DC (published online)
70-80% of the HVDC platform cost is down to the structure
Only one platform, highly complex, platforms are late and undergo commissioning problems, whole wind farm power transmission is dependant on it

## Slide 4: HD MMC for Platform-less Offshore HVDC System
Features:
HVDC power transmission from the very beginning
  Reduce losses and components (at system level)
Decentralised multi-terminal HVDC system
  Increase availability – Offers flexibility and redundancy
  Reduce cost – Removal/minimise offshore substation
Objective: Develop a dedicated high fault tolerances, flexible and cost effective power collection technology for offshore wind industry
Notes: Dolwin Beta (dolwin 2) HVDC converter station.
916MW, 320kVdc, 155kVac, 45km (offshore to shore) + 92km (onshore to substation), 1400mm2 Cu XLPE transmission cable
http://www.4coffshore.com/windfarms/hvdc-converter-dolwin2-converter-cid11.html
Converter (top side) of the station:
Weight: 10,000 tonnes
size: 100.1m x 74m
Losses – cable transmission losses; component reduction at system level and removal of Ac platform, Reactive power compensation, cooling.
More testing can be done onshore helping cost savings.

## Slide 5: Converter topology analysis – HB/HB, HB/MMC, MMC/MMC
Optimum configuration found to be HB-MMC at 1.4 kHz
Majority of losses attributed to converter conduction losses
This can be decreased by moving to 3-phase
Different converter configurations modelled in Simulink
  HB-HB
  HB-MMC
  MMC-MMC
Based on input waveforms, the transformer specifications are optimised and losses calculated
Repeated for frequencies between 500 – 2,000 Hz
Notes: Frequency problems with converters
Optimise the design of HVDC transformer
Done insulation studies (transformer winding insulation and connection to DC array cables)

## Slide 6: HB-MMC Harmonic Interaction
Chart: 
Large Harmonic disparity between HB and nL MMC
  Power control issues (harmonics)
  Transformer hotspots (potentially)
MMC on LVDC bus requires few modules therefore same issue
Traditionally use PWM and filter but in MF, high switching losses result!
Chart: 
X
HB
nL MMC

## Slide 7: The Modular Multilevel Converter
Its modular design makes it ideal for scaling up.
    Now used in a variety of applications, including HVDC
Very attractive for offshore wind
    Low THD on AC terminal therefore no bulky filters
    High efficiency
    High degree of controllability

## Slide 8: The Modular Multilevel Converter (MMC) Limitations
Each module can only create one AC voltage level Lconv:
Therefore many modules required to reduce THD < 3 % (≈ 30)
Each module requires two valves and a large capacitor
    Capacitor contributes to roughly 50 % of the module volume
Therefore achieving low THD increases converter losses and more crucially converter’s size and weight
A LARGE offshore platform is required to support it.
Platform structure accounts for ≈ 70 % of substation cost therefore significant savings possible by reducing size or elimination

## Slide 9: The High Definition Modular Multilevel Converter
By using the novel HD-MMC control algorithm one module corresponds to multiple AC voltage levels
Using the HD-MMC algorithm only 12 modules are required to create 29 L
This is achieved by grouping modules into sets, controlling each to provide additional voltage levels
Therefore fewer modules for the same THD
This results in a more compact converter reducing platform size and cost
Reduce modules
Reduce modules
Group
into sets
Group
into sets
Notes: Unlike standard MMC where one module is one AC voltage level
Modules in a set are controlled to the same DC voltage level
Each set controls modules to a different DC voltage level compared to another set, e.g. 600Vdc, 300Vdc, 150Vdc

## Slide 10: The High Definition Modular Multilevel Converter Control
Standard 15L MMC
Number of AC voltage step levels will increase by:
Number of IGBT modules for 3 phase MMC:
72 vs 168
Switches/Valves
More saving on higher MMC level
Standard 15L MMC
Synthesized AC Voltage
Standard 7L MMC
Synthesized AC Voltage
Save > 55% on MMC module
Notes: AC voltage step levels equation refers to HD-MMC approach
Second equation calculates IGBT modules for 3 phase (specifically the number of switches if you assume two per module)
Graph shows the extreme savings on MMC if the number of levels and switches is very large
HD-MMC could achieve the output of 15L MMC with same number of modules as 7L MMC - >55% module saving

## Slide 11: Proposed HD-MMC Control
Non intrusive, the HD-MMC control algorithm (red) can be inserted as an add on to the standard control methods (blue) of the MMC.
This simplifies implementation

## Slide 12: Conclusion
HVDC is more cost effective and practical over long distances
HVDC substation structures are very expensive
  Through use of the Hybrid HVDC Transformer, it can be eliminated
The HD-MMC approach was developed to optimise the Hybrid Transformer
It offers huge cost and volume saving potential through improved utilisation of the MMC’s hardware

## Slide 13: Recent Work/Next Steps
Developing HVDC grid topology and control for Hybrid HVDC Transformer concept
  Grid cluster (five turbines in series with some redundancy)
Optimising HD-MMC control algorithm for low module count
Looking at 3-phase implementation of Hybrid HVDC Transformer
More detailed cost analysis of Hybrid HVDC Transformer
Collaboration being finalised with SINTEF and IREC (part of IRPWind project)
  To demonstrate HD MMC concept on hardware – beyond simulation (SINTEF laboratories)
  Validation of software models against hardware results
  Medium scale (significant laboratory scale test) – 780VDC, 60kW converter
Notes: Grid cluster – 5 five turbines in series – some redundancy (can afford to lose 2 in a set of 5)
Protection – No DC CB suitable at the moment; not a standard HVDC grid and going in one direction 99% of the time. If there is a serious fault, we would cut off the wind farm and can isolate individual turbines via btb converter, then isolate AC side and allow DC bus to decay naturally. Preferable to adding redundancy through additional dC transmission lines and DC CB due to cost – in discussion with TenneT

## Slide 14: Research Outcomes
Publications:
M. Smailes, Chong Ng. P. Mckeever, R. Fox, M. Knos, J. Shek “A modular, multi-megawatt, hybrid HVDC transformer for offshore wind power collection and distribution” EWEA Offshore conference, Copenhagen, March, 10-12, 2015
M. Smailes, C. Ng, R. Fox, J. Shek, M. Abusara, G. Theotokatos and P. Mckeever, “Evaluation of core loss calculation methods for highly non- sinusoidal inputs” IET ACDC Conference, Birmingham, UK, February, 10-12, 2015
Michael Smailes, Chong Ng, Jonathan Shek, Girasimos Theotokatos, Mohammad Abusara, “Evaluation of Core Loss Calculation Methods for Highly Non-sinusoidal Inputs”, 13th Wind Integration Workshop, Berlin, Nov 2014
M. Smailes, C. Ng, J. Shek, G. Theotokatos, M. Abusara, “Hybrid, multi-megawatt, medium frequency HVDC transformer for offshore wind turbines”, Renewable Power Generation Conference (RPG), Naples, Sept 2014
Chong Ng, Paul McKeever, “Flexible HVDC Transformer for Next Generation Renewable Energy Industry”, Journal of Energy and Power Engineering ,vol. 7, no. 9, Sept 2013, pp. 1625 – 1633
Chong Ng, Paul McKeever, “Offshore Renewable Plant HVDC Power Collector and Distributor”, 22nd International Conference and Electricity Distribution (CIRED), Stockholm, June 2013
Chong Ng, Paul McKeever, “Next generation HVDC network for the offshore renewable energy industry”, The 10th International Conference on AC and DC Power Transmission, Birmingham, Dec 2012
Patent Applications:
Smailes M., Ng C., “Low component count, low loss, Modular Multilevel Converter design for HVDC”, pending UK Patent application 2014
Smailes M., Ng C., “Low component count, low loss, Modular Multilevel Converter design for HVDC”, pending PCT Patent application 2014
Ng C. H., Southern D., Ferguson A. D., “A Power Collection and Distribution System”, WO2011033308, published 24th March 2011