## Slide 1: Wind-Farm-Scale Measurements Using Mobile-Based LiDAR
M. Zendehbad, N. Chokani, R.S. Abhari
ETH Zurich, Switzerland
WindEurope Summit 2016
27 September 2016

## Slide 2: Overview
Introduction
Objectives
Approach
Results
Conclusions

## Slide 3: Introduction
  Wind turbines operating in wakes result in upto 20% losses in wind farms
  Higher turbulence in wakes results in increased maintenance of wind turbines (Zendehbad et al., Renewable Energy, 2016)
  As wind and water tunnels do not simulate all full-scale non-dimensionals, field measurements of wakes and their impact are necessary.

## Slide 4: Operational Limitations Hinder Wide-Spread Usage of LiDARs
LiDARs measure line-of-sight component (LOS) of wind speed
In previous work, authors demonstrated wind-farm-scale measurements of LOS wind speed using single LiDAR
  Present work extends method to wind-farm-scale measurements of 2D wind field
200m
Wind
Radial speed (m/s)
-8 8
Line-of-sight direction
Wind
Zendehbad et al., J. Solar E. Engineering, 2016

## Slide 5: Objectives
Demonstrate mobile-based LiDAR measurements of Cartesian velocity field on scale of wind farm
Quantify impacts of wake on wind farm performance

## Slide 6: Mobile Laboratory Equipped with LiDAR
Custom-built mobile laboratory, windRoverII, designed at ETH and equipped with 3D scanning LiDAR system to measure wind field
LiDAR head
LiDAR system | 
Model | Galion LRI
Accuracy | 0.25m/s
Angular resolution | 0.1o
GPS
- position
Magnetic sensor
- heading
Dual-axis tilt sensor
- attitude
Data acquisition and control unit
- Data assimilation and processing
- Wind velocity vector
LiDAR
- line-of-sight wind speed
- azimuth and elevation angles

## Slide 7: Measurements Made at 25.8MW Wind Farm
25.8MW wind farm located in northern Germany
  9 turbines of three different types
  Flat agricultural land
Primary wind direction during measurement is 150o
Siemens SWT3.6
Vestas V90
Vestas V80
200m
Wind
WEA1
WEA2
WEA3
WEA4
WEA5
WEA6
WEA9
WEA8
WEA7
Turbine | Hub height (m) | Rotor diameter (m) | Rated power (MW)
Siemens SWT3.6 | 93 | 107 | 3.6
Vestas V90 | 105 | 90 | 3.0
Vestas V80 | 60 | 80 | 2.0

## Slide 8: Flow Field in Wind Farm Scanned from 11 Positions
Wind farm flow field scanned from 11 positions
Fully automated software :
  determines optimum scanning positions
  specifies positions to driver
  determines scan pattern at each position
  visualises real-time measurements
Siemens SWT3.6
Vestas V90
Vestas V80
Measurement position
200m
Wind
1
2
3
4
5
6
7
8
9
10
11
Optimum Scanning positions
roads
wind direction
LiDAR’s maximum range
wind farm layout
Optimum Scanning positions
Autonomous Measurement System

## Slide 9: Measured Horizontal Wind Speed Shows Multiple Wakes in Wind Farm
Wakes with average maximum deficit of 52% measured
Wakes extend in different directions
Horizontal wind speed (-)
1
0
Wind
H = 60m AGL
H = 93m AGL
H = 105m AGL
Vestas V90
Siemens SWT3.6
Vestas V80
Hub heights
Vertical profile of wind direction shows wind veer of 13deg. per 100m
Wind veer explains differences in directions of wakes
Siemens SWT3.6
Vestas V90
Vestas V80

## Slide 10: Wake Extent Impacts Power Generation
Simultaneous power generation from SCADA data shows:
  39% underperformance of WEA1 due to direct impact of wake from WEA2
  Over-performance of WEA5 and WEA6 that operate between wakes
Wind
WEA1
WEA2
WEA3
WEA4
WEA5
WEA6
WEA7
WEA8
WEA9
Horizontal wind speed (-)
1
0

## Slide 11: Rotor Yaw Misalignment Results in Underperformance
Turbine WEA2 has 6% less power than turbine WEA4
Measurements at 2D downstream of WEA2 show wake is laterally offset by 0.3D
  Lateral offset of wake can be consequence of rotor yaw misalignment explaining underperformance of turbine WEA2
Normalised power | 
WEA2 | WEA4
0.94 | 1
Siemens SWT3.6
Vestas V90
Vestas V80
200m
Wind
WEA2
WEA4

## Slide 12: Simulations Show Good Agreement with Measurements
Predictions of in-house Reynolds-Averaged Navier-Stokes solver with Immersed Wind Turbine Models shows good qualitative agreement with measurements
  Inflow
  Outflow
  Rotor
  Immersed Wind Turbine Model
Predictions
Normalized streamwise speed
0 1
Wind
Normalized streamwise speed
0 1
Measurements

## Slide 13: Wake Recovery is Accurately Predicted
Excellent quantitative prediction of wake recovery downstream of turbine WEA5 with 5% RMS difference compared to measurements
Wind
WEA5
Horizontal wind speed (-)
1
0

## Slide 14: ETH Semi-Empirical Wake Model Shows Good Agreement with Measurements
ETH Wake Model is semi-empirical model based on sub-scale experiments in ETH wind turbine test facility
Predicted spanwise velocity deficit at 2D shows good agreement with full-scale measurements with only 6% RMS difference
Spanwise position, Y/D
U/Uref
ETH Wind Turbine Test Facility

## Slide 15: Conclusions
Measurements of Cartesian velocity components on scale of wind farm demonstrated using mobile-based LiDAR
  this measurement approach can be readily deployed to assess performance in actual wind farms
Impacts of multiple wakes on turbine performance was quantified
Observed that wake skewness due to rotor yaw misalignment is also a source of underperformance
CFD and wake model predictions show very good agreement with measurements