## Slide 1: Comparison of Uncertainties in Wind Resource Assessment With and Without On-Site LiDAR measurements: A Cast Study
Wind Europe 2016 Session: LIDARs – the zapping competition Tuesday, 27 Sept, 2016
Edward Burin des Roziers, Anaïs Madaule,
Jérémy Tahar, Stéphanie Pham, Julien Leon
Acknowledgements: wpd Leosphere

## Slide 2: Outline
Introduction
Two wind measurement strategies
Comparisons of results
Summary
Notes:   It’s no secret that UL is a global force for good that has been working to promote safe living and working environments for more than a century
    We’ve been a leading standards development organization since the dawn of electricity
    And we’ve been advancing safety breakthroughs and addressing the risks associated with every wave of innovation including electronics, petrochemicals and sustainability
    We work collaboratively with our customers to design, produce, package and sell safer products around the world
    And we consistently fulfill our safety mission by acting in ways that reinforce our ethical values, respect people, empower communities and support the natural environment

## Slide 3: Purpose of Case study
Energy yield assessments today rely on data predominantly from measurement masts.
    Requirement for building permits (delays in project development)
    Higher installation effort than for RSD
Recently revised guidelines (*) allow for Remote Sensing Devices (RSD) under certain conditions.
    The RSD type must be classified
    The RSD must be calibrated (verified) next to high quality mast in simple terrain before the measurement campaign.
    Most often used in combination with an on-site measurement mast -> good correlation with the reference mast.
    In the case of no on-site measurement mast, the RSD must also be post-calibrated after the campaign
Case study: energy yield assessment where a LiDAR was incorporated in the measurement strategy.
* Measnet: Evaluation of site-specific wind conditions v2, April 2016
FGW TR6 Rev. 09, August 2013
(CD) IEC 61400-12-1 Ed. 2 Power performance measurements of electricity producing wind turbines, June 2016

## Slide 4: Project Site
DRAFT
8 km

## Slide 5: On-Site Measurements
 | Mast | LiDAR
Manufacturer | Thies First Class Adv. Thies First Class (vanes) | Leosphere Windcube v2
Measurement period | 2 years | 6.5 months
Measurement heights | 85.25 m (v, v) 82.00 m (dir) 62.00 m (v) 60.00 m (dir) 40.00 m (v) | 180 m, 160 m, 150 m, 140 m, 120 m, 104 m, (v, dir) 100 m, 85 m, 80 m, 60 m, 58 m, 42 m
Elevation (m) | 107 m | 72 m
System Availability (before filtering, across all measurement heights) | 99.50% | 95.50%

## Slide 6: Outline
Introduction
Two wind measurement strategies
Comparisons of results
Summary
Notes:   It’s no secret that UL is a global force for good that has been working to promote safe living and working environments for more than a century
    We’ve been a leading standards development organization since the dawn of electricity
    And we’ve been advancing safety breakthroughs and addressing the risks associated with every wave of innovation including electronics, petrochemicals and sustainability
    We work collaboratively with our customers to design, produce, package and sell safer products around the world
    And we consistently fulfill our safety mission by acting in ways that reinforce our ethical values, respect people, empower communities and support the natural environment

## Slide 7: Two approaches to wind measurement strategy
Approach 1: Mast Only
Correction of mast data with long-term data source (MERRA)
Wind characteristics at target site (~8 km) (WASP)
Calculation of turbine production and uncertainties
Exceedance probabilities
Approach 2: Mast + LiDAR
Extension of LiDAR data to 2 years using mast data (MCP)
Correction of LiDAR data with long-term data source (MERRA)
Wind characteristics at target site (WASP)
Calculation of turbine production and uncertainties
Exceedance probabilities

## Slide 8: Sources of Uncertainties
    Uncertainties important for this specific case study
    1) From LiDAR:
      Measurement uncertainties related to the classification and calibration
    2) From MCP:
      Assessment of the quality of correlations between the LiDAR and the reference mast
    3) From spatial extrapolation:
      Spatial extrapolation (both vertical and horizontal) from mast location to target site

## Slide 9: RSD Classification (CD) IEC 61400-12-1
Classification:
The type of RSD device must be classified
Correlations of wind speeds
Sensitivity to environmental variables (non-exhaustive list):
Uncertainty on wind speed:
  In this case:
where an accuracy class of 3.3 was used*.
*Classification of Windcube V2, Deutsche WindGuard, 2013
  Wind shear exponent
  Turbulence intensity
  Rain
  Wind direction
  Air temperature
  Air density
  Temperature difference between two heights
  Upflow angle
Notes:   It’s no secret that UL is a global force for good that has been working to promote safe living and working environments for more than a century
    We’ve been a leading standards development organization since the dawn of electricity
    And we’ve been advancing safety breakthroughs and addressing the risks associated with every wave of innovation including electronics, petrochemicals and sustainability
    We work collaboratively with our customers to design, produce, package and sell safer products around the world
    And we consistently fulfill our safety mission by acting in ways that reinforce our ethical values, respect people, empower communities and support the natural environment

## Slide 10: RSD Calibration (Verification) (CD) IEC 61400-12-1
In this case, a calibration test was performed with the same mast before measurement campaign.
Correlations of wind speeds
Direction, shear and turbulence
Calculation of uncertainties
Notes:   It’s no secret that UL is a global force for good that has been working to promote safe living and working environments for more than a century
    We’ve been a leading standards development organization since the dawn of electricity
    And we’ve been advancing safety breakthroughs and addressing the risks associated with every wave of innovation including electronics, petrochemicals and sustainability
    We work collaboratively with our customers to design, produce, package and sell safer products around the world
    And we consistently fulfill our safety mission by acting in ways that reinforce our ethical values, respect people, empower communities and support the natural environment

## Slide 11: Uncertainties of measurements of RSD (CD) IEC 61400-12-1
In summary, uncertainties on the wind measurements of RSD include:
RSD calibration test (includes reference sensor uncertainties) (L.4.2)
RSD classification test (none, if LiDAR remained at calibration site) (L.4.3)
Non-homogeneous flow within measurement volume (L.4.4)
Mounting effects of the RSD (L.4.5)
Variation in flow across the test site (L.4.6)
Possible uncertainties from unexpected monitoring of the RSD (L.5.2)

## Slide 12: MCP (Measure – Correlate – Predict)
Why are we allowed to use MCP in this case?
Half-year measurement period of the LiDAR covers relevant seasons
High correlation between the mast and the LiDAR (R² = 0.77 on 10min basis)
Reliable extrapolation of the site measurements
Uncertainties considered in MCP :
Difference in measurement height
Distance between site and reference measurement
Terrain type (orography, roughness)
Quality (R², results of extrapolation)
Representativeness

## Slide 13: Outline
Introduction
Two wind measurement strategies
Comparisons of results
Summary
Notes:   It’s no secret that UL is a global force for good that has been working to promote safe living and working environments for more than a century
    We’ve been a leading standards development organization since the dawn of electricity
    And we’ve been advancing safety breakthroughs and addressing the risks associated with every wave of innovation including electronics, petrochemicals and sustainability
    We work collaboratively with our customers to design, produce, package and sell safer products around the world
    And we consistently fulfill our safety mission by acting in ways that reinforce our ethical values, respect people, empower communities and support the natural environment

## Slide 14: Uncertainties
Sensitivity of the turbines to the site, uncertainties of power curve,
farm efficiency

## Slide 15: Exceedence Probabilities
Caution: other sites may behave differently!

## Slide 16: Considerations for Representativeness of Case Study
Uncertainties in classification and calibration
  Quality of correlation
  Quality of assessment
Uncertainties of installation
  Making use of installation protocols
  Avoiding obstacles in the path of the LiDAR beams
  Proper levelling and orientation of the RSD
Correlation with reference mast
  Consideration of mast – LiDAR distance
  Consideration of site topography
Data availability
Representativeness of measurement period
  Need for capturing seasonal effects

## Slide 17: Outline
Introduction
Two wind measurement strategies
Comparisons of results
Summary
Notes:   It’s no secret that UL is a global force for good that has been working to promote safe living and working environments for more than a century
    We’ve been a leading standards development organization since the dawn of electricity
    And we’ve been advancing safety breakthroughs and addressing the risks associated with every wave of innovation including electronics, petrochemicals and sustainability
    We work collaboratively with our customers to design, produce, package and sell safer products around the world
    And we consistently fulfill our safety mission by acting in ways that reinforce our ethical values, respect people, empower communities and support the natural environment

## Slide 18: Summary
Slight increase in measurement uncertainties for this site for the LiDAR based approach.
Additional uncertainties due to the use of MCP on LiDAR data.
But
Additional measurement and MCP uncertainties were much lower than spatial extrapolation uncertainties.
A significant reduction of uncertainties and increase in P90 was possible in this case by including an RSD in the wind measurement strategy.

## Slide 19: Thank you.