## Slide 1: Power performance optimization and loads alleviation with active flaps using individual flap control
Vasilis Pettas
Thanasis Barlas
Drew Gertz
Helge Madsen

## Slide 2: Outline
Introduction
DTU 10MW RWT upscaling
Aeroelastic model & flap implementation
AEP controller
Fatigue controller
Integrated controller
Results
Conclusion
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”

## Slide 3: Introduction
Modern wind turbine blade technology enabling rotor upscaling
Active aerodynamic load control as potential enabling technology
Active flap system development
INDUFLAP & INDUFLAP2 projects
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: -Trend in the industry the rotor upscaling to reduce LCOE .
-Active aerodynamic control (smart rotor concepts) being researched as potentially enabling technology.
-The Adaptive Trailing Edge Flaps is one of the most promising with a lot of focus being given in the research.
-Experience in DTU with the INDUFLAP projects.

## Slide 4: Introduction
Aeroservoelastic load simulations
Wind tunnel testing
Field testing
Active flap system development
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: WHAT HAS BEEN DONE in the flap research
-engineering models developed ATEFlap and aeroservoelastic load simulations carried out
-Testing of airfoil in wind tunnel and small scale turbine tests have shown the proof-of-concept
-two full scale tests and a rotating rig have been done showing the potential
-Rubber Flap system developed closer to industrial implementation (reliable and robust, hinge-less/ morphing shape, advanced pneumatic actuators)

## Slide 5: DTU 10MW RWT upscaling
DTU 10MW RWT
5% blade upscaling/stretched – other components same
Solidity, twist, airfoils, structural properties same – ‘softer’ blades
Earlier pitching to reduce max thrust – same rated power
Using flaps to target baseline design fatigue load envelope
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: -Present work is done in a business case framework considering applicability and robustness
-DTU 10MW conceptual RWT rotor was upscaled 5% keeping the same rated power
-The blades where only changed with main aerodynamic (aerodynamic similarity) and structural ND properties kept the same leading to stretched softer blades
-Earlier pitching introduced to decrease max steady thrust to baseline levels
-The resulting topology and operating characteristics of the turbines can been seen along with the resulting increase in fatigue loads
-AEP +3.4% for 10% TI and fatigue were evaluated according to IEC standard and DLC 1.2 for normal production
Whether or not the fatigue loads in main components (tower bottom, blade root, nacelle, main bearing) can reach the original fatigue load envelope and on parallel increase power production

## Slide 6: Aeroelastic model & flap system
HAWC2
ATEFlap dynamic stall model
Flap servo
DLL controllers
30% blade’s spanwise length-single flap
+/-15deg flap deflection
10% chord coverage
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: Aeroelastic modelling done with the DTU in-house aeroelastic tools. HAWC2 with ATEFlap dynamic stall model implemented modeling the flap aerodynamics as well simulating the flap’s servo 1st order LP filter.
-The flap servo is modeled as a 1st order LP filter
-Control implemented through fortran DLLs
-Flap is covering 30% of the blade (26m) in the outboard part of the blade.
-Covering the 10% of the chord
-The morphing trailing edge flap deflection as shown here is between-15/15 degs
-Aerodynamic characteristics with CFD simulations using ellipsys in-house tool

## Slide 7: AEP controller
Flap action based on LP filtered local angle of attack (feedforward)
Individual flap angle assignment
Gains based on CL=f(alpha,beta) polar
Tunable flap offset angle
Parametrical sweep based optimization (offset and actuator dynamics)
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: -The controllers where developed separately for the two objectives (AEP and fatigue reduction) and then combined
AEP Part
-Feed forward individual flap controller based on the LP filtered mid-flap local angle of attack (measured with an inflow or pressure sensor).
-Based on the known polar (optimal Cl/Cd ratio) and assuming linear slope in the operating region for all flap angles an optimum flap angle beta was found based on parametrical sweeps for all speeds giving the optimal offset flap angle.
-Moreover time constant (accounting for the phase difference between flap action and actual changes in aerodynamic forces) was considered a parameter and the optimal for all below rated speed was found.
So single input-single output feedforward IFC

## Slide 8: Fatigue controller
PD on high-pass filtered blade root flapwise moment (feedback)
Gain tuning using Ziegler-Nichols method and parametrical sweeps per speed
Based on closed-loop HawcStab2 models
PD gains scheduled over LP filtered wind speed
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: The second controller aiming for the fatigue loads, as has been seen in previous studies also.
-It is a individual flap Proportional Derivative controller based on the HP flapwise blade root bending moment input.
-The PD gain tuning for each wind speed was based on ZN rule with stability points derived from the linear closed loop state space representation of the system derived with HawcStab2 and parametrical sweeps.
-These gains were then scheduled with linear interpolation based on LP wind speed.
-Parametrical sweeps for servo’s time constant.
So IF feedback PD control based on HP filtered blade root flapwise bending moment input and gain scheduling with LP filtered wind speed (can be obtained directly from measuring instrumentation or indirectly from main controller’s operating point).

## Slide 9: Integrated controller
AEP controller below rated
Fatigue controller above rated
Smooth switching based on LP filtered WSP and signal from main controller
Tunable flap servo response
Flap controller applied on top of main controller
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: -After finding optimal parameters and individual application based on IEC DLC 1.2 simulations, the two controllers where combined with the AEP operating below rated and the fatigue above (where most of the fatigue is contributed in most of the components).
-The switching being smooth and efficient was tuned based on LP filtered wind speed and a LP signal full load indicator from main controller showing the operational point.
-The controller is completely decoupled and on top of the main controller.
-The optimal values for the switching were found with parametrical sweeps which also helped understanding the systems behavior
-Tested in DLC 1.2

## Slide 10: Results – AEP increase
AEP increase (below rated)
Influence of turbulence intensity
AEP increase due to upscaling for 10% TI : 3.4%
Influence on fatigue loads
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: Results regarding power production:
-The results in terms of power production for different TI values varying from steady state to IEC IA turbulence show that the effect is decreasing as TI increases varying from 0.1-0.4 % for this highly optimized conceptual rotor (study of commercial rotors showed higher increase) where in industry numerical power curves are considered with a 10% TI giving 0.2% increase and in total including the upscaling 3.6%.
-Results shown include, as in IEC, 6 turbulence seeds per speed with a 1 m/s discretization.
-This control objective shows a small increase in fatigue loads mainly in tower channels.

## Slide 11: Results
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Animation of bade and flap response
DLC 1.2 8m/s – AEP feedforward IFC
no flap
flap

## Slide 12: Results – fatigue load alleviation
Fatigue load reduction above rated
Focus on design blade loads and main bearing
AEP part increases loads below rated
Class specific results (IA)
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: The fatigue part of the controller targets only above rated operational points.
-As seen in the figure mainly MxBR and main bearing channels reduced to the original baseline level.
-Tower bottom for-aft channel is increased mainly due to the fact that a higher percentage of the fatigue is contributed from around rated speeds.
-Blade root torsion is inevitably increased due to the increased pitching moment coming from the flaps (usually not a design load though…).
-The SEL figure shows the clear trade of the channels negatively influenced are in the AEP regime which along with each speed’s contribution to lifetime fatigue can give a good overview of the system’s behavior.
Next we can see an animation of the PD fatigue controller

## Slide 13: Results
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
no flap
flap
Animation of bade and flap response
DLC 1.2 22m/s – Fatigue PD IFC

## Slide 14: Conclusions
In terms of AEP the IF feed-forward control can increase AEP depending on the level of aerodynamic optimization, site-specific shear and TI
The fatigue margin of the baseline design should be taken into account in order to evaluate sufficiency of platform
Possible integration of different control objectives with some trade-offs
Robust and easy to apply approach. No significant increase to pitch activity.
The presented control approach enables further rotor upscaling
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Future work
Extreme load alleviation – integration of objectives
Evaluation of real system on Siemens 4.0-130 (INDUFLAP2)
Notes: The main conclusions are:
In terms of AEP the proposed method showed potential depending on the level of the original rotor\s optimization and the site specific wind conditions.
Fatigue load alleviation mainly blade root flap and main bearing. The fatigue margin has to be taken into account in order to see if the upscaling for these components is feasible
It is seen that the different control objectives can be combined. This is enabler for different methods to be combined it shows that different objectives and different methods (azimuth related, different input channels) can be combined like extreme load, parking, gusts, stand still etc.
The sensors used are already used by the industry and the simple control schemes are less prone to errors provided that the inputs are accurate
Enabling rotor upscaling in many different ways. The upscaling can be done even simpler with ideas like tip extension and flap in order to reduce even more RD costs or integrate it in the whole turbine design process so that (main controller, aerodynamic design, flap actions, load restrictions) are all optimized together. Also other concepts like individual pitching or passive control can be combined towards a more efficient rotor.
Future work includes
-Investigation of more objectives with the flap system like the extreme load alleviation and possible integration
-A full scale test will be carried out on a real system (Siemens 4.0) as well as test in the rotating rig in DTU-Riso

## Slide 15
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Thank you for your attention
Questions?