## Slide 1: Grid integration and stability of 600MW windfarm at Kriegers Flak
The largest power plant in Denmark
Vladislav Akhmatov
Energinet.dk – Transmission System Operator of Denmark

## Slide 2: Motivation and innovation of Kriegers Flak
The 600 MW wind power plant will be the largest power production unit in Denmark
It will be connected to two 400kV substations in the Danish onshore transmission system
The offshore and onshore connection network will be a meshed HVAC system which includes two platforms
The offshore system continues towards Germany (not part of this presentation)

## Slide 3: Introduction
Energinet.dk is Transmission System Operator of Denmark for electricity and natural gas
Denmark is one country, but two HVAC systems which are asynchronous to one another and linked via HVDC

## Slide 4: Present status
Denmark is blessed by wind power:
Over 6000 turbines with over 5000 MW total capacity;
Approx. 47% of electrical energy over one year is produced by wind power
Source: Energistyrelsen (Danish Energy Authority)
Wind turbine technology by power capacity:
o Greater than 3 MW / WTG
o 1 … 3 MW / WTG
o 0,5 … 1 MW / WTG
o Smaller than 0,5 MW / WTG

## Slide 5: Kriegers Flak and Denmark East
Outlook 2020 | Capacity [MW]
Comsumption | 900…2843
Onshore wind | 894
Offshore wind | 372
Kriegers Flak OWF | 600
Photovoltaic | 255
Decentral Thermal | 315
Central Thermal | 1940 (max. 450)
Great Belt HVDC | 600/600
Kontek HVDC | 600/600
HVAC to Sweden | 1700/1300

## Slide 6: Kriegers Flak grid-connection
220kV cables, 80km
Expected WTGs:
Converter-interfaced;
Grid-code compliant;
LVRT;
Q or U control in MV point of reference.
220kV cable, 34km
220kV cable, short

## Slide 7: System Stability Assessment
Transmission system model:
  400kV system with substations, lines and cables,
  400/132kV transformers at 400kV substations,
  132kV system with substations, lines and cables,
  132/50kV and 132/10kV transformers at 132kV substations,
  Part of 50kV distribution network with 50kV substations,
  Fully- dynamic models of HVDC connectors.
Dynamic models and control of:
  Central power plants,
  Synchronous compensators,
  A Static VAR Compensator,
  Large wind power plants including control and LVRT,
  Individual and aggregated models of onshore wind turbine sites, PV modules, CHP units, consumption centers.
Commercially-available simulation tool PowerFactory/Digsilent.

## Slide 8: System Stability Assessment
Bus-bar short-circuits:
  400kV substations,
  100 ms duration,
  post-sequent trip of adjacent components.
Operation Scenarios – this becomes normal for Denmark-East:

## Slide 9
Comparison:
read - U (voltage) control,
blue - Q (reactive power) control.
Learning objective:
Both control options are stable.
Faster voltage recovery at U control.
Less repeating LVRT at U control.
Excessive LVRT entering may cause trip.
0 2 4 6 8 t[s] 10
0 2 4 t[s]
0 2 4 t[s]
U[pu]
1.25
0.25
Response of Kriegers Flak
P[MW]
250
0
Q[Mvar]
200
-50

## Slide 10: Conclusion
The Kriegers Flak windfarm will become the largest power unit in Denmark.
Denmark becomes the transmission system where the largest power unit is a windfarm.
Demonstration of dynamic voltage stability with no central power plants in-service.
Relevance of LVRT, voltage-control mode and grid-code compliance for keeping dynamic stability.

## Slide 11: Thank you! And a quick question?