## Slide 1: Uncertainty Quantification of the Real-Time Reserves for Offshore Wind Power Plants
Tuhfe Göçmen
Gregor Giebel
Pierre-Elouan Réthoré
Juan Pablo Murcia Leon
Jesper Runge Kristoffersen Vattenfall
PossPOW & Concert

## Slide 2: Outline
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Introduction to Reserve Power & Balancing Market
Estimation of Real Time Reserves for Offshore Wind Power Plants
  PossPOW Algorithm
  Wind Farm Scale Available Power
    ‘Normal’ Operation
    Down-Regulation
      Experiments in Horns Rev-I
  Data based ‘Objective’ Uncertainty Quantification of the estimated reserves
  Conclusions & Future Work

## Slide 3: Reserve Power & Balancing Market
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Additional Active Power and / or demand reduction by the TSOs
  Upregulation (Potential) and / or Down-regulation (Mandatory)
    Available (or Possible) Power
    Balancing market and /or Compensation
Belgium : Elia  WF scale available power signal is requested and potentially evaluated @ 15mins
Germany & the Nertherlands : TenneT  Both turbine and WF level. Detailed data collection and quality check @ 15mins
Ireland : EirGrid  Quality check via RMSE < 6% of the maximum capacity @ 15mins
The UK : National Grid  WF scale available power signal is a part of the Grid Code now. Quality check @ 10mins according to “Good Industry Practice”
Denmark : Energinet.dk  Data collection @ 5mins, quality check @ 15mins. The error should be within ±5% of the actual power
Notes: Peter Sorknæs showed that the up-regulation potential is really cost-effective  study in Sund & Bælt turbines, profit is 196%
The TSOs are responsible for the quality of the reserves : says ENTSO-E
The UK : the grid code will be in operation starting from 1 April 2016
Denmark: Deviations are calculated using the most recent, entire day of normal operation on the same site

## Slide 4: Current Real-time Reserves vs. PossPOW
“Good Industry Practice” in WF Scale 
  However,
    Down-regulated turbine  Down-regulated wake
    More energetic flow downstream
    Higher wind speed @ the downstream turbine(s)
   Higher available power
PossPOW  correction of the reduced wake during DR
  Local Wind Upstream
    Rotor Effective Wind Speed Estimation
  Advection of Wind Through the Wind Farm
    “Real-time” wake model
    Local Turbulence Intensity
    WF dynamic effects : Time delay & Meandering
  Validation
    Dedicated experiments in Horns Rev-I

## Slide 5: PossPOW Algorithm

## Slide 6: PossPOW Algorithm
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Wind Farm Power – Horns Rev I
Percentage Error in Wind Speed – Thanet
Notes: Using approximated Cp curve, as in the effective WS estimation  since the manufacturer power curve is standard, 10-min data & 10% incoming TI
24 hours dataset  mainly northwesterly wind – diagonal wakes (not as strong)
Higher hit rate due to smoother wind direction
The WS inside the WF is highly variant! Almost 4m/s bin!  production varies aling downstream, PossPOW still performs good.

## Slide 7: PossPOW Validation
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Down-Regulation Experiments in Horns Rev-I
Photo courtesy : Vattenfall & Hasager, Charlotte Bay, et al. "Wind farm wake: The Horns Rev photo case." Energies 6.2 (2013): 696-716.
in normal operation:
due to upstream curtailment:
what should be in normal operation:
Notes: Curtail the test turbine for the perpendicular wind direction – assume the power production between two neighbouring rows would be the same under those conditions  similarity assumption

## Slide 8: PossPOW Validation
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Down-Regulation Experiments in Horns Rev-I
Notes: Normal wind direction - westerly or southerly. The ±WD is defined after 21 days of historical data examination  app. 20deg bin for the westerly winds, broader in the stop trigger
WS below rated + high enough to establish downstream wind to be higher than the cut-in
All the turbines are downregulated to 500kW, lowest limit for the V80 turbine regardless of the WS
6 experiments in total
Data also shows that most of the difference between the rows are due to the atmospheric turbulence (std of WD checked)  will briefly discussed later

## Slide 9: PossPOW Validation
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Down-Regulation Experiments – Wind Speed
Notes: 50 mins of curtailment
2 wake events took place: 1) without DR, 2) with DR – between grey lines
1st wake downstream agreement is good in no DR
2nd wake, more wind at the curtailed downstream

## Slide 10: PossPOW Validation
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Down-Regulation Experiments – Wind Speed
Notes: The disagreement among the downstream turbines under DR is recovered with the PossPOW Algorithm
The reduced wake due to curtailment is corrected!

## Slide 11: PossPOW Validation
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Down-Regulation Experiments – TSO Requirements
Notes: Checked wrt Energinet.dk regulations since most detailed and the most conservative so far
Only 2 turbines in the row  make the most of the similarity assumption and avoid local TI effects
The experiments have different upstream WS, TI etc  rather wide scope to evaluate the PossPOW algorithm performance

## Slide 12: PossPOW Uncertainty
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
15 mins Provision – Error distribution
Total 6 experiments
Notes: Emphasize how (more) wrong using just the SCADA would be
in the operations monitoring for off-performance conditions!

## Slide 13: PossPOW Uncertainty
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Real-time (1 sec) – Error distribution
Total 6 experiments
Notes: Emphasize how (more) wrong using just the SCADA would be
in the operations monitoring for off-performance conditions!
In total 8 hours data – all downregulation experiments (fish)
Uncertainty = half the size of 16th - 84th percentiles

## Slide 14: PossPOW Uncertainty
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
30 sec Provision – Error distribution
Total 6 experiments
Notes: Uncertainty = half the size of 16th - 84th percentiles
Only 960 data points on total  hence bootstrapping

## Slide 15: PossPOW Uncertainty
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
30 sec averaged data - Bootstrap Error distribution
Circular block bootstrapꜞ
ꜞ Politis, Dimitris N., and Joseph P. Romano. "A circular block-resampling procedure for stationary data." Exploring the limits of bootstrap (1992): 263-270.
Notes: Uncertainty = half the size of 16th - 84th percentiles
Block length of the bootstrap = 2  corresponding to (30sec x2 = 1min)

## Slide 16: ConCERT : Control and Uncertainties in Real-Time Power Curves of Offshore Wind Power Plants
Add Presentation Title in Footer via ”Insert”; ”Header & Footer”
Notes: WP1 : Preparation & Market Integration & Lit. Review
WP2 : Estimation & Mitigation of uncertainty in Available Power
WP3 : Multi-objective WF Control
WP4 : Experimental Verification & Trading Market Aspects
WP0 : Management and Dissemination

## Slide 17: DTU Wind Energy at WindEurope Summit 2016: Stand 574, Hall B6