## Slide 1: Challenges of integrating Variable Renewable Energy Sources (V-RES)
2016-09-27, WindEurope Summit 2016, A. Oudalov, C.Y. Evrenosoglu, A. Marinakis, A. Timbus

## Slide 2: Challenges of integrating V-RES
What it is about?
Based on results of the internal study titled Power Grids of the Future.
Analysis framework is capable to address phenomena from ms to years.
Notes: We develop a quantitative evaluation framework and examine possible scenarios of electric power sector transition.

## Slide 3: Challenges of integrating V-RES
Table of contents
Global trends towards renewable power grids.
Technical challenges of integrating large amount of variable renewables (V-RES).
Technology options to expand grid flexibility.
Key take-away points.
Utilities and grid operators need to become more flexible to accommodate more variable renewables.

## Slide 4: Changing power sector
Power balance tipping irreversibly towards renewables, driven by policy & disruptive technology cost reduction.
The main growth is foreseen in variable renewables - wind and solar.
We identify two paths:
  centralized renewables (C-RES),
  distributed* renewables (D-RES).
Some industrialized regions incline towards the distributed renewables path.
Fast-developing regions mainly follow the centralized renewables path.
Power balance tipping irreversibly towards renewables
*units <50 MW connected to MV and LV distribution grids.
Chart: Distributed generation (DG)* contribution to annual total demand [%]
| 18 | 26 | 36
Germany, Energiewende | 32.5 | 41 | 63
India, 5-years dev't plan | 17 | 24 | 40
China, Government plan | 17.8 | 26.8 | 38
D-RES
C-RES
100% central
RES
100% distributed
RES
Source: Energiewende, China and India official plans, ABB analysis

## Slide 5: What can happen when large amount of V-RES is online?
Technical challenges may limit the proliferation
Germany may operate in the critical zone due to strong connections to the ENTSO-E grid.
Ireland limits an instantaneous percentage of non-synchronous resources by 50%.
* Percentages are dependent upon system characteristics
Chart: Year
| 41274 | 41639 | 42004 | 42369 | 42735 | 44196 | 47848 | 51501
y_IN | 5 | 5 | 5 | 6 | 8 | 20 | 70 | 78
IN | -0.5 | -0.5 | -0.5 | -0.5 | -0.8 | -4 | -21 | -27.3
y_DE | 42 | 54 | 58 | 63 | 69 | 84 | 115 | 209
DE | -0.9 | -0.6 | -0.5 | -0.6 | -0.6 | -4.2 | -11.5 | -41.8
y_CN | 4 | 5 | 7 | 9 | 11 | 20 | 48 | 104
CN | -0.5 | -0.5 | -0.7 | -0.7 | -0.55 | -3 | -9.6 | -26
y_US | 0 | -1 | -2 | -3 | -2.45 | -5.5 | -7 | -7
US | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -2 | -8 | -20
y_JP | -2 | 0 | 3 | 6 | 9 | 23 | 27 | 23
JP | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -3 | -10 | -15
Today
Normal
Fair
Critical
Serious
Source: ABB analysis
Max hourly V-RES [%]* | Technical challenges
>100 |  + significant variable RES curtailment
75-100 |  + short circuit power
50-75 |  + system inertia & grid voltage
25-50 | grid capacity & reserve
0-25 | normal operation

## Slide 6: Technical challenges may limit V-RES proliferation
Impacts of system inertia evolution on system stability
Increasing penetration of V-RES is leading to changes in ROCOF and frequency nadir following a disturbance.
Example: frequency response of the Nordic system to tripping of a 750 MW generator.
For aggregated inertia the critical clearing time (CCT) is 228 ms.
Source: H.R. Chamorro, M. Ghandhari, R. Eriksson, Wind Power Impact on Power System Frequency Response. 2013

## Slide 7: Technical challenges may limit the proliferation
Impacts of system inertia evolution on system stability
For if a disturbance is cleared after 228 ms the system is unstable.
The fault has to be cleared much faster to maintain a stable operation.
For aggregated inertia (scenario without V-RES) the CCT is 228 ms.
We reduce to due to a large amount of V-RES on-line (55% in that specific case).

## Slide 8: Technical challenges may limit the proliferation
Impacts of system inertia evolution on system stability
For the CCT must stay below 130 ms (40% faster).
In order to keep the fault must be cleared even faster, at most in 73 ms.
For aggregated inertia (scenario without V-RES) the CCT is 228 ms.
We reduce to due to a large amount of V-RES on-line (55% in that specific case).

## Slide 9: A need for more flexible system
Technology options at different system levels
Max. hourly variable RES %* | Technical challenges | Technology options at different power system levels |  |  | 
 |  | Prosumer | Distribution | Transmission | Generation
>100 |  + significant variable RES curtailment |  |  |  | 
75-100 |  + short circuit power |  |  |  | 
50-75 |  + system inertia & grid voltage |  |  |  | 
25-50 | grid capacity & reserve |  |  |  | 
Converter control
Small battery
Sector coupling
DSM
Wholesale, retail, AS
Market based options
Platform based options
Wholesale, AS, cap.
Microgrids, VPP
Next generation SCADA/EMS, WAx, DMS
Hydro storage
Flexible units (coal, natural gas, nuclear)
Converter control
Synchronous condenser
Interconnectors (HVDC)
FACTS
Utility battery (>50 MW)
Medium battery
Supercap, flywheel
LVR, D-STATCOM
Power to fuel
Faster protection
Adaptive protection
* Percentages are dependent upon system characteristics
Enabling technologies
Flexible generation sources
Energy storage
Flexible demand
DSM – demand side management, LVR – line voltage regulator, D-STATCOM – distributed static compensator, AS – ancillary services, VPP – virtual power plant, WAx – wide area monitoring, control, protection,

## Slide 10: Challenges of integrating V-RES
Key take-away points
Technical challenges may hamper the large scale proliferation of variable renewables unless existing power grid product and system requirements and the rules of grid operation are revisited.
Transmission and distribution grids will need to be increasingly more accommodating to dynamically changing generation profiles.
Emerging business models based on extensive use of ICT infrastructure facilitate market participation of DER.