## Slide 1
Low level jets,
Intermediate
boundary layers
and veer:
accommodating
real world wind shear
In established procedures

## Slide 2
Low level jet
Wake

## Slide 3
“Scanning lidar” is a very powerful instrument. It provides
  Information we would not otherwise have
  Earlier access to information we can get other ways

## Slide 4
Variable azimuth
Variable elevation
Complex scan geometry
Simple scan geometry
Multiple beams
Lidar methods
There is a wide variety of lidar methods

## Slide 5: IEA Use Cases
Clifton, A. et al., IEA Wind Energy Task 32 Remote Sensing of Complex Flows by Doppler Wind Lidar: Issues and Preliminary Recommendations, NREL, 2015
Measurement method
Data acquisition situation
Data requirements

## Slide 6: IEA Use Cases
What measurement accuracy is verified in this situation?
What data requirements arise in this situation?
What measurement method fulfils my data requirements?

## Slide 7
© Gerrit Wolken-Möhlmann, Fraunhofer IWES

## Slide 8
Galion G4000 Offshore on transition piece
2 x Galion G4000 Offshore on nacelle, one facing forward to survey inflow, one facing back for wakes
© Gerrit Wolken-Möhlmann, Fraunhofer IWES

## Slide 9: Unit G24

## Slide 10: Low level jets: why is shear important?

## Slide 11: Low level jets: why is shear important?
Cyclical fatigue loads at the blade root if blade pitch is not adjusted for varying conditions
Large torque variance on the drive shaft impacting gearbox life.

## Slide 12: Low level jets: why is shear important?
IEC 61400-1:2005
Wind Turbines Part 1:
Design requirements
Chart: 
Height / hub height
Wind speed / hub height wind speed

## Slide 13: Low level jets: why is shear important?
IEC 61400-1:2005
Wind Turbines Part 1:
Design requirements
Chart: 
Height / hub height
Wind speed / hub height wind speed
Shear is described by a single parameter
Veer is completely ignored

## Slide 14: What is a low level jet?
Chart: Wind speed (m/s)
| 7.4742462431746919 | 8.2359101726757302 | 8.7169464389325775 | 9.0751915531716083 | 9.363176334504729 | 9.6052478758822115 | 9.8147926141677253 | 10 | 10.166263292249333 | 10.317331903845572 | 10.455923033967567 | 10.584071773697556 | 10.703343691705076 | 10.814970192819388 | 10.919938138336121 | 11.019051158766107 | 11.112972785665772 | 11.202257531078136 | 11.287373755651704 | 11.368720807044408 | 11.446642075120012 | 11.521435082340954 | 11.593359385100431 | 11.662642834242572 | 11.729486588843226 | 11.794069170875472 | 11.856549773637497 | 11.917070983520741 | 11.975761036150143 | 12.032735699688683 | 12.088099857160497 | 12.14194884395047 | 12.194369584749367
Shear 0.14 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330
LLJ Profile 1 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330
LLJ Profile 2 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330
Chart: Wind speed (m/s)
| 7.4742462431746919 | 8.2359101726757302 | 8.7169464389325775 | 9.0751915531716083 | 9.363176334504729 | 10.5 | 11.5 | 12 | 12.5 | 12.3 | 11.5 | 11 | 10.703343691705076 | 10.814970192819388 | 10.919938138336121 | 11.019051158766107 | 11.112972785665772 | 11.202257531078136 | 11.287373755651704 | 11.368720807044408 | 11.446642075120012 | 11.521435082340954 | 11.593359385100431 | 11.662642834242572 | 11.729486588843226 | 11.794069170875472 | 11.856549773637497 | 11.917070983520741 | 11.975761036150143 | 12.032735699688683 | 12.088099857160497 | 12.14194884395047 | 12.194369584749367
LLJ - Loading case 1 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330
LLJ - Loading case 2 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 | 210 | 220 | 230 | 240 | 250 | 260 | 270 | 280 | 290 | 300 | 310 | 320 | 330
Baas1, 2009 – 20% reduction above hmax
Alternative – shear coefficient > 0.4 calculated with hub height and top tip wind speeds
Schematic representations of LLJs for illustrative purposes
The height hmax at which maximum wind speed occurs relative to the rotor influences shear across the rotor
1Baas, P., et al., A climatology of nocturnal low level jets at Cabauw, Journal of Applied Meteorology and Climatology, Volume 48, August 2009

## Slide 15: Incidence of LLJs as defined by Baas
Over one third of the time the height of the LLJ is 210 m amsl

## Slide 16: Incidence of LLJs as defined by Baas
A clear diurnal pattern is observed in the incidence of LLJs identified using the Baas criterion.

## Slide 17: Incidence of LLJs

## Slide 18: Load equivalent wind shear exponent
Chart: Frequency of occurrence (%)
| -0.2 | -0.1 | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
 | 0.0039586 | 0.011571 | 0.19245 | 0.43666 | 0.16108 | 0.069123 | 0.039281 | 0.027101 | 0.014921 | 0.013094 | 0.0054811 | 0.0039586 | 0.014007
5 to 10%

## Slide 19: Load equivalent wind shear exponent
Chart: Frequency of occurrence (%)
| 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 19
-0.2 - 0 | 6 | 5 | 7 | 3 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
0 - 0.2 | 243 | 259 | 253 | 170 | 160 | 201 | 220 | 169 | 101 | 53 | 21 | 13 | 4 | 3 | 1
0.2 - 0.4 | 60 | 59 | 40 | 70 | 38 | 67 | 87 | 69 | 94 | 64 | 23 | 12 | 5 | 1 | 0
> 0.4 | 56 | 65 | 34 | 46 | 44 | 16 | 21 | 8 | 1 | 1 | 2 | 0 | 0 | 0 | 0

## Slide 20
Chart: 
| -10 | 10000
 | -10 | 10000
Frequency of load
Severity of load
Fatigue loads
Extreme loads
LLJs, etc.: intermediate load scenarios neglected by current wind turbine design guidelines

## Slide 21: Wind turbine wake interactions

## Slide 22: Wind turbine wake profiles
Chart: 8-10 m/s
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.0515323717769169 | 1.0358684725691665 | 1.010983049864447 | 1.0154311614250273 | 1.0049650731737341 | 1.004204376688032 | 1.0106745726881232 | 1.0044508975004367 | 0.99692554919059617 | 1.004826167717116 | 1.0055579754613662 | 1.0037253739646035 | 0.98941855543620605 | 1.0012212722944702 | 1.0058195354996873 | 1.0002478865265594 | 0.98416158563106315 | 0.97614598828766763 | 0.98126062859810659 | 0.96786457745690446 | 0.96159279259891306 | 0.90794486753488479 | 0.67121252320965519
2.23 RD upwind of AV07 | 295 | 285 | 275 | 265 | 255 | 245 | 235 | 225 | 215 | 205 | 195 | 185 | 175 | 165 | 155 | 145 | 135 | 125 | 115 | 105 | 95 | 85 | 75 | 65 | 55 | 45 | 35 | 25 | 15 | 5
4.27 RD downwind of AV07 | 295 | 285 | 275 | 265 | 255 | 245 | 235 | 225 | 215 | 205 | 195 | 185 | 175 | 165 | 155 | 145 | 135 | 125 | 115 | 105 | 95 | 85 | 75 | 65 | 55 | 45 | 35 | 25 | 15 | 5
6.24 RD downwind of AV07 | 295 | 285 | 275 | 265 | 255 | 245 | 235 | 225 | 215 | 205 | 195 | 185 | 175 | 165 | 155 | 145 | 135 | 125 | 115 | 105 | 95 | 85 | 75 | 65 | 55 | 45 | 35 | 25 | 15 | 5
4.57 RD downwind of AV05 | 295 | 285 | 275 | 265 | 255 | 245 | 235 | 225 | 215 | 205 | 195 | 185 | 175 | 165 | 155 | 145 | 135 | 125 | 115 | 105 | 95 | 85 | 75 | 65 | 55 | 45 | 35 | 25 | 15 | 5
6.57 RD downwind of AV05 | 295 | 285 | 275 | 265 | 255 | 245 | 235 | 225 | 215 | 205 | 195 | 185 | 175 | 165 | 155 | 145 | 135 | 125 | 115 | 105 | 95 | 85 | 75 | 65 | 55 | 45 | 35 | 25 | 15 | 5

## Slide 23: Alleviation of loads
Elevated loads that impact component lifetime include:
  Flap-wise blade root bending moment
  Gearbox torque variance
Alleviation of loads can be achieved through Individual Blade Control (IBC), e.g. ATLAS offered by SgurrControl
Strain gauge data from each blade is used to align pitch of each blade individually
Loads can be reduced to within design limits during extreme and complex shear events

## Slide 24: Alleviation of loads

## Slide 25: Thank you for listening
Email: peter.clive@sgurrenergy.com
Tel: +44 (0) 141 227 1724
Cell: +44 (0) 7739 909 040
Web: http://www.sgurrenergy.com