## Slide 1: Icing losses
Carla Ribeiro
WindEurope - Wednesday 28 September 2016
Energy
what can we learn from production and meteorological data

## Slide 2: Agenda
Meteorological data – what have we learned from looking at 70+ masts in Cold Climate
Production data – what have we learned from looking at 20+ wind farms in Cold Climate
    Influence of control strategy
    IAV
    Influence of elevation
How to estimate icing losses using the lessons above
    Elevation
    Meteorological data
    Long-term adjustment
Notes: The agenda for today’s webinar includes:
An overview of our presenter.
Icing:
  Meteorological and instrumental icing of instruments during a measurement campaign.
  Operational production losses.
  Benefits of icing prevention systems (including de-icing and anti-icing).
Cold weather driven atmospheric stability:
  Challenges to wind flow modelling and the benefits of stable CFD.
  The impact on turbine performance.
Brief discussion about the use of remote sensing in pre-construction measurement campaign.
A question and answer session.

## Slide 3: Meteorological data – what have we learned from looking at 70+ masts in Cold Climate

## Slide 4: 1 Meteorological and instrumental icing of instruments during a measurement campaign
Temperature ˚C
Relative Humidity %

## Slide 5: 1 Meteorological and instrumental icing of instruments during a measurement campaign
Analysed data from over 70 masts and 500 sensors.
Linear relationship between instrumental icing and elevation.

## Slide 6: 1 Meteorological and instrumental icing of instruments during a measurement campaign
Different icing zones across the Nordics.
Zones related to longitude.
Elevation the biggest driver within a zone.

## Slide 7: Production data – what have we learned from looking at 20+ wind farms in Cold Climate
Influence of control strategy
IAV
Influence of elevation

## Slide 8: 2 Operational production losses - Data analysed
Analysed SCADA data from 20+ wind farms in the Nordic region 365+ turbines (spanning 6 to 7 years).
Reasonable geographical coverage:
  12+ projects in Sweden.
  <5 Projects in Norway.
  <5 Projects in Finland.
Excludes projects where icing loss is managed manually.
Includes projects where:
  Turbines that shut down when controller detects icing.
  Turbines that remain operational during blade icing events.

## Slide 9
Influence of control strategy
Question: What’s the potential benefit of keeping turbines operational during icing events?
Method:
  Simulate energy losses which would have been incurred during icing for projects which remain operational during icing events.
  Compare actual to simulated losses.
  Assumptions about sensitivity of controller ice detection required.
Impact on loads not considered.
2 Operational production losses

## Slide 10
Inter-annual variability
Question: How much do icing losses vary from year to year?
  Derive monthly icing loss for each wind farm.
  Calculate annual icing loss (July to June) based on nominal production profile.
  Only projects with very long operating periods useful.
  Inter-annual variability (IAV) defined by the coefficient of variation.
High mean loss coincides with low variability.
Low mean loss coincides with high variability.
Very long datasets required to accurately determine long-term mean losses.
2 Operational production losses

## Slide 11
Importance of elevation
Questions: How do icing losses vary with altitude?
  Individual turbine mean annual losses calculated.
  Correlation of loss vs. effective hub-height.
Strong relationship between loss and elevation throughout Sweden.
Coastal Norway and Finland do not follow trend of Swedish sites, although data-sets are small.
2 Operational production losses

## Slide 12: How to estimate icing losses using the lessons above
Elevation
Meteorological data
Long-term adjustment

## Slide 13
A. Icing loss climatology
Relationship of annual icing loss and elevation used to define icing climatology.
  Represents loss for projects were turbines remain operational through icing events.
Geographical coverage limited by:
  Data availability.
  Reliability of loss / elevation relation.
  General experience of factors driving icing: cloud base elevation, Arctic / Siberian weather systems, Atlantic / Gulf stream effect.
Uncertainty in loss estimate needs to be recognised.
  High variability inevitable leads to high uncertainty.
  Confidence elevated due to good length of datasets (6+ years) in combination with geographical diversity.
3 How to estimate icing losses

## Slide 14
cannot be directly measured from typical met masts
B. Methodology
small amount of icing = low severity
large amount of icing = high severity
given by
anemometer
data
3 How to estimate icing losses

## Slide 15: 3 How to estimate icing losses
Validation

## Slide 16
C. Long-term correction?
Based on temperature and humidity data from nearby reference stations:
    Uses a matrix methodology.
Comparison of the frequency of icing conditions during the measured period relative to a longer historical period.
Challenging as reference source must be representative!
3 How to estimate icing losses

## Slide 17
High inter-annual variability – 80%
Suggests upward adjustment of 60%
Significant uncertainty -
used with care!
3 How to estimate icing losses

## Slide 18: Conclusions and further work
    Elevation
  Elevation can be used as a proxy for icing loss in Sweden
  Initial results suggest the relationship is not applicable to Finland and coastal Norway.
  More data required to patch gaps in Sweden, and understand Norwegian and Finish conditions.
  Further wind farms being analysed and interesting results for turbines in wakes or behind hills
    Meteorological data
  DNV GL has a validated method for reliably converting anemometer data to the expected annual energy loss for areas not covered by the map.
    Long-term adjustment
  Inter-annual variability in icing losses is very high.
  Measurement period in excess of 5 years required to reduce loss prediction error below 2% of AEP.
  DNV GL has a method to extrapolate historical data and assess the iciness of site measurements relative to the long-term expectations
  Further validation work is under way for the long-term adjustment
    Control strategy
  Great potential for reducing energy loss by keeping turbines operational through icing conditions, rather than shutting down.
  Relative benefit diminishes with increasing icing loss.
Notes: The agenda for today’s webinar includes:
An overview of our presenter.
Icing:
  Meteorological and instrumental icing of instruments during a measurement campaign.
  Operational production losses.
  Benefits of icing prevention systems (including de-icing and anti-icing).
Cold weather driven atmospheric stability:
  Challenges to wind flow modelling and the benefits of stable CFD.
  The impact on turbine performance.
Brief discussion about the use of remote sensing in pre-construction measurement campaign.
A question and answer session.

## Slide 19: Additional information
  Quantification and estimation of Energy Losses caused by blade icing using SCADA data and pre-construction meteorological masts in the Nordic region, Till Beckford, Staffan Lindahl, Carla Ribeiro (Winterwind 2015 and updated at Winterwind 2016).
  Performance of NWP-based ice loss predictions for resource assessment – a roadmap for improved validation as a crucial element in the model development process, Daran Rife, Gemma Daron (Winterwind 2016).
  Quantifying the impact of ice accretion on turbine life for typical Scandinavian sites using numerical modelling, John King, Ricard Buils Urbano (Winterwind 2016).
  DNV GL Memo, Key information required on turbine de-icing and anti-icing systems, Carla Ribeiro.
  A study of turbine performance under cold weather driven stable atmospheric conditions, Carla Ribeiro, Ben Buxton (Winterwind 2014).
Thank you
carla.ribeiro@dnvgl.com | Direct +44 (0) 203 816 5565