## Slide 1: Line voltage regulators offer an innovative approach to increasing the capacity of distribution grids to accommodate wind power
Frank Cornelius - ABB Transformers - WindEurope Summit 2016

## Slide 2
Local community / investor wants to install 3x2 MW wind power on near-by hills
A request for connection to the existing 20 kV distribution grid is submitted to the electric utility
grid had 4 MV feeder lines
total length of grid: 48.4km
number of MV/LV transformer stations: 117
max. load: 10.3 MW
max. in-feed: 6.9 MW
After analysis, utility refuses to connect since the allowed max. voltage gets exceeded in feeder 4
6 MW
feeder 1
feeder 2
feeder 3
feeder 4
SS: 110/20kV
Line voltage regulator for MV distribution grids
What is the problem ?
Notes: Picture from “geography” internet: http://www.geograph.org.uk/photo/828640 and http://www.geograph.org.uk/photo/3010207 free licence for using: http://creativecommons.org/licenses/by-sa/2.0/

## Slide 3
Present situation
Installation of wind turbines does not have an effect on the voltage in the other feeders.
Due to other feeders (load characterized) the tap setting of the HV/MV transformer can not be changed!
With 6 MW additional infeed, the voltage strongly exceeds the permitted voltage band
The thermal load of the cables is uncritical: 70% Ir
The load case remains uncritical
Situation with additional 6 MW wind turbines
Line voltage regulator for MV distribution grids
Voltage profile in feeder 4

## Slide 4
The line voltage regulator “recalibrates” the voltage
The voltage stays within the allowed range in the whole distribution grid
LVR in medium voltage grid
Line voltage regulator for MV distribution grids
How can a line voltage regulator solve the problem ?

## Slide 5
The 3x2 MW wind turbines can be connected to feeder 4 - no reinforcement of the MV distribution grid is needed
No influence on the line protection system thanks to small impedance of the LVR
Realization within several months
Potential for an additional turbine: adoption of the LVR voltage set point, placement of the LVR closer to primary SS
Situation with additional 6MW wind turbines …and with additional line voltage regulator
V [%]
Line voltage regulator for MV distribution grids
Line voltage regulator installed in feeder 4
LVR

## Slide 6: How does a line voltage regulator work ?
Single line diagram
transformer
V
MV or LV line
UL
UB
UR=UL-UB
URB
line voltage regulator
MV or LV feeder
loads and decentralized generation
UL: line to ground voltage
UB: booster voltage on line side
URB: booster voltage on regulator side
UR: regulated line to ground voltage
Notes: Ausbessern rechte Winkel und so )

## Slide 7: Line voltage regulator for MV distribution grids
Main technical data
* rated power of the line
** contact ABB for exact value of rated power at 36kV
*** different values available on request
Rated power* | MVA | 14 | 30
Voltage** | kV | up to 36 | 
Frequency | Hz | 50 or 60 | 
U regulation range |  | +/-8% | +/-4%
Step voltage*** |  | 1,6% | 0,8%
Number of steps*** |  | 11 | 11
# switching operations |  | >1’000’000 | 
Energy efficiency |  | >>99% | 
Control mode |  | fixed voltage or power flow dependent | 
Operation mode |  | automatic or via SCADA | 
LVR mounted and fully tested in concrete compact substation

## Slide 8: Line voltage regulator installation Installation in a MV-grid
Chart: 
Voltage (kV)
The Line Voltage Regulator reduces the large voltage variations and adjusts the voltage to a regular level.
The integration capacity of grids increases for the integration of decentralized energy sources.
regulated LVR output voltage
LVR input U
voltage at HV/MV SS
8 MVA 20 kV

## Slide 9: A line voltage regulator …
controls voltage rise or drop
allows to feed additional wind power into existing grids
available for single turbine or wind farm installations
is often the better economic solution than grid extension
doesn’t influence the protection system
can be realized fast
makes existing grids flexible for changing infeed of wind and other decentral generation