## Slide 1
Wind Europe Summit 2016 | Hamburg | 27.09.2016
Dr.-Ing. Mark Meuser
M. Sc. Christoph Schönhofen
Utilizing fluctuating feed-in characteristics of WEC for grid integration
Notes: Thank you for your kind introduction, Mr. Chairman,
Good afternoon ladies and gentlemen,
I will use the next round about 12 min. to present to you the basic idea, methodology and results of a research project conducted at FGH last year. The project is about utilizing the highly fluctuating feed-in of WEC and PV for the purpose of grid integration. Due to the lack of time i won‘t go to much into the details, but you may look up missing information in the conference proceedings and of course i will be available afterwards for any questions.

## Slide 2: Introduction
Significant increase of number / installed power of wind energy converters (WEC) in electrical distribution grids (mainly MV)
Local concentration of installed power driven by wind conditions etc.
Especially in windy regions the further development of WEC-Installations is limited by available capacities for grid connection
Conventional method: grid reinforcements driven by single grid connection request or already foreseeable grid connection projects
  High costs and long operating lifetimes of grid components vs.
  Future local development and especially deployment hardly predictable
   Risk of developing long term inefficient grid structures
Improved utilization of existing grid structures
  Flexibility
  Cost efficiency
  Short-term implementable solutions
Notes: In the past 15 years and still ongoing we have a significant increase ..
Aditionally we see a local..
Therefore especially ..
The conventional method to adress this issue is to do grid..
Involving high costs..
Resulting in a significant risk to
Our solution to solve this problem is an improved utilization of ..
aiming at flexible, ..

## Slide 3: Analysis
Limiting criteria for grid connection of WEC typically given by boundaries for steady-state grid voltage and (thermal) loading of grid components
  Limits for steady-state grid voltage acc. 50160 given for 99% of 10min.-mean-RMS-values
  Loading capability of earth-buried cables/transformers depending on load characteristics with thermal inertia of several hours  time dependency and modelling of state transition
  Load flows influenced by
    Fluctuating active power feed-in of WEC and other generating plants (PV etc.)
    Residential and industrial consumers
    Consideration of mutual dependencies by correlation
    Controlled reactive power provision of WEC/PV
    Tab-position of OLTCs etc.
Time-dependent probabilistic approach with discrete time steps of 10-15min. and thermal models for state transition
Notes: Among the criterions for assesment of grid connection of WEC typically the limitations for steady-state grid voltage as described in EN50160 and the limitations regarding the maximum admissible loading of lines and transformer proof to be the most critical ones.
The limits for grid voltages described in EN50160 refer to 99%... Which leads to a probabilistic approach using steady-state load flow calculation with time steps of about 10min.
Anyway the loading .. depends on the loading the component is subject to for serveral hours, meaning one has to consider the time dependency of consecutive states appropriately. Obviously because of the high thermal inertia compared to the required step size, state transition models for the thermal behaviour of earth-buried cables and transformers are required. They are modeled as step responses, with the steps given by the changes of loading in consecutive steady-states / time steps.
Generally the load flows are subject to ..
So to sum up a time dependet .. was chosen.

## Slide 4: Analysis
Grid integration methods considered
  Improved utilization of existing options for grid operation
    Improved control concepts for transformers with OLTC
      Wide-area-control (voltage regulation at distant network nodes)
      Load flow dependent voltage set-point
    Extension of range and optimised control of reactive power provision by WEC
    Improved utilization of loading capability reserves of grid components given by thermal inertia especially of earth buried lines and transformers
  Introduction of additional options for grid operation by actively controlled (variable) components
    Use of MV / LV transformers with OLTC
Notes: Based on the fact, that steady-state voltage and loading issues in general turn out to be most critical for grid integration of WEC a variety of methods which adress these issues were developed and considered. They can be rougly classified in those using already existing options for grid opertation as improved OLTC control.. ,furtherly extended range and optimized control of .. OR improved utilization of loading ..
On the other hand there are methods introducing additional actors and therefore options for grid operation … such as ..

## Slide 5: Methodology
Generation of time series for customer installations
Calculation of hosting capacity
Calculation of max. admissible loading of lines&transformers
Load flow calculation with minmal load
Grid data Markov- und Distance-Matrices
Time series for
WEC PV MV customers sub-stations
Allocation of feed-in/load time series to customer installations / sub-stations
Loading
Temperature
Calculation for each grid component
Voltage
Violation of limit?
Reduction of installed power
Yes
No t < tEND
No t = tEND
t = 0
Inrease of installed power
Iz = max. admissible current under consideration of calculated load characteristic
Im=1 = rated current
Notes: The developed methodology is schematically shown in this slide. In a first step input data for the monte carlo simulation in terms of time series for every generating plant, industrial customer and sub-station as described before is automatically generated using second order markov chains. In a second step the maximum admissible installed power of the generating plants in the given scenario is calculated iteratively using heuristic optimization algorithms. Grid integration methods as described before are taken into account in this step.
Besides calculating this so called hosting capacity for the given scenario the max. admissible current over all time steps is used to calculate the newly introduced value f_total. Further information on this value will given in the after next slide.
All these steps are repeated some thousand times to make shure every statistically relevant state was considered.

## Slide 6: Exemplary results
Total hosting capacity for WEC / PV in an exemplary rural MV-grid
Typical extended rural grid  Initially hosting capacity limited by steady-state voltage boundaries
Innovative voltage regulation strategies improve HC until limits of loading capability are reached (if voltage issues are entirely resolved)
Consideration of temporary overload capabilities enables further increase of HC without any additional costs
Chart: Hosting capacity
| Ohne Regelung | Q(U) | rONT | Ferner Knoten
Installierte Leistung NS | 15.5949 | 15.5949 | 15.5949 | 15.5949
Ohne Temperaturmodell | 4.5749 | 9.3632 | 9.9183 | 9.502
Mit Temperaturmodell | 0 | 1.2322 | 7.2963 | 6.043
Pinst,LV
Pinst,MV
MW
Conventional planning Q(V) MV/LV-OLTC Wide-area control
Notes: On this slide some exemplary results for the total hosting capacity for generating plants in an extended rural MV-grid are shown using some of the introduced grid integration methods.
The lower part represents the maximum admissible installed power in the supplied LV-grids, whereas the upper dark blue part of the columns represent the maximum admissible installed power of generating plants connected to the MV-grid without consideration of overloading reserves of earth-buried lines and transformers. It can be seen, that initially the hosting capacity of the grid ist limited by steady-state voltage issues since even a simple optimization of the reactive power control of connected power plants using a voltage dependent characteristic allows for a significant increase of the HC. When using voltage control concepts in rural grids and in general when talking about urban and suburban grids it won‘t be the voltage causing worries but the loading of lines and transformers. Anyway using the thermal reserves especially of grid components with high thermal inertia such as earth-buried cables and transformers an additional gain may be reached without any costs, in this example represented by the upper red part of the columns.

## Slide 7: Load factor under consideration of volatile load characteristics
Conventional daily cyclic loading characteristic only valid for conventional distribution networks without significant share of WEC / PV
Fluctuating feed-in characteristics of wind turbines and photovoltaic systems lead to deviating load profiles
Conventionally defined load factor not appropriate when assessing the real loading capacity of grid components as earth-buried lines / transformers
Solution: Determination of the maximum permissible loading, taking into account thermal inertia of (earth-buried) lines and transformers
Chart: 
Chart: 
Chart: Belastungsgrad
Mo
Di
Mi
Do
Fr
Sa
So
Mo
Di
Mi
Do
Fr
Sa
So
Mo. Tu. We. Th. Fr. Sa. Su. Mo. Tu. We. Th. Fr. Sa. Su.
Consumer
Photovoltaics
WEC
Load factor
Notes: Typical residential as well as industrial consumers show – at least when aggregated on MV-level – a daily cyclic load profile, slightly modified at weekends. For that reason it is common practice to use the so called load factor , describing the relation between mean load and peak load in a period of 24h, for assessment of potential overloading reserves, typically assuming an aggregated load factor of 0.7.
Anyway fluctuating feed-in .. As shown in this figure, where the load factor ist hypothetically calculated with respect to the last 24h for an aggregated consumer load, PV and WECs. Especially for WEC there is no 24h-cyclic characteristic, so the conventionally ..
However, in distribution grids with a significant or even dominant share of WECs or PV

## Slide 8: Summary
Especially in windy regions the further development of WEC-Installations is limited by available capacities for grid connection
Conventional grid reinforcements are cost-intensive, cause significant project delays and may lead to long term inefficient grid structures even if embedded in an appropriate long term planning scheme
Improved utilization of existing network structures using the fluctuating feed-in characteristics of WECs
  Improved transformer control concepts
  Temporary overloading capabilities of earth-buried cables and transformers
  Extension of range and optimized control of reactive power provision by WEC
  MV / LV transformers with OLTC
Limiting criteria for grid connection of WEC typically given by boundaries for static grid voltage and (thermal) loading of grid components
Time-dependent probabilistic approach with discrete time steps of 10-15min. and thermal models for state transition
Results
  Conventional load factor not appropriate for assessing loading capability of grid components in distribution grids with a significant share of WEC / PV
  Innovative voltage control concepts and consideration of temporary overloading capabilities allow significantly increased hosting capacity in a wide variety of distribution grids
Notes: Please allow me to summarize my presentation and point out some key findings.
Especially ..
For that reason some methods for improved utilization .. Were developed and analyzed such as
It was shown that the limiting ..
Therefore a time-… was chosen
Exemplary results show that..
Please note, that these results were obtained for a variety of exemplary grids and scenarios but should be furtherly verified by additional studies.
Thank you for your kind attention.

## Slide 9
Wind Europe Summit 2016 | Hamburg | 27.09.2016
Dr.-Ing. Mark Meuser (mark.meuser@fgh-zertifizierung.de)
M. Sc. Christoph Schönhofen (christoph.schoenhofen@fgh-ma.de)
Thank you for your attention!

## Slide 10
BACKUP

## Slide 11: Modeling
Consideration of mutual dependences by correlation
Assessment of static system states
  15-min mean values sufficient
20 (10) kV
0,4 kV
Correlation WEC/PV distance dependence
Correlation PV in LV distance dependence
Voltage dependence of the load
110 kV

## Slide 12: Specific criteria for the assessment of grid connection of WEC
Thermal current carrying capacity
  Assessment of grid capacity for continuous load (load factor = 1)
Static voltage limits (according to EN 50160)
  Limits for grid voltage at the point of common coupling of customer installations
  Assessment based on statistical criteria
Short-circuit current
  Grid coupling via converters: short-circuit current contribution of WEC rather small
   Simple countermeasures: short-circuit-current-limiters
Grid disturbances
  Fast (switching) changes in voltage / flicker
  Harmonics / interharmonics / ripple-control
   Use of filters / modification of inverter frequency and/or inverter control
Limiting criteria for grid connection of WEC typically given by limits for static grid voltage and thermal loading of grid components

## Slide 13
Aa
  Aa
    Aa
      Aa
        Aa
Aa
  Aa
    Aa
      Aa
        Aa