## Slide 1
Low temperature compliance testing
of wind turbine applications for the
‘cold climate’ market
pieterjan.jordaens@owi-lab.be
www.owi-lab.be

## Slide 2
Sirris - collective technology centre in Belgium
  Supporting companies with implementing technology innovations
  Multidisciplinary R&D and innovation projects in technology industry
  Different technology sectors: Automotive, Energy, Aerospace, ICT, …
  Different key expertise: ICT, Manufacturing, Mechatronics, Materials
  High-tech test and R&D infrastructure
Introduction
OWI-Lab - RD&I center for wind energy in Belgium
  Set-up in 2010 as a new application lab at Sirris to support wind energy R&D
  Scope: wind energy in general - focus on ‘offshore wind’ and ‘cold climate’
  Range of new and unique test & monitoring infrastructures
  Partnership with 3 Belgian universities for wind energy research (VUB, KU Leuven, UGent)
  Member of IEA Wind Task19 Wind Energy in Cold Climates

## Slide 3
Unique test infrastructure – large climate chamber
Public large climatic test chamber for wind turbine applications (+60°C to -60°C / Humidity / IR-Solar load)
Focus: climatic validation tests of wind turbine equipment (cold, hot-tropical and offshore climates)
Full size small & mid-range wind turbine nacelle (or assembly) tests
Power electronics tests
Pitch & Yaw cold starts
Hydraulic brake tests
Generator tests
Functional component testing with or without wind turbine auxiliaries (forced cooling, pumps, heating, expansion tank, lubrication unit,…)
Electrical, mechanical and hydraulic components as
gearboxes, transformers, switch gears, power electronics, anti & de-icing systems,…
R&D tests on the behavior of fluids, oils and hydraulics in a full functional set-up

## Slide 4
Driver for the ‘testing topic’ within the wind power business
1
2
Source: Fraunhofer IWES
Attention point: wind turbine need to be fitted for the job to work in challenging environments:
Cold Climate, Hot Climate, Tropical Climate, Offshore
Essential part in the product development cycle
Notes: Failure avoidance is key in the quest of lowering the LCOE

## Slide 5
Purpose of prototype testing in the climate chamber
FMEA Process – Pillay and Wang 2003
Design validation
Checking if simulation models are valid (model validation)
Risk mitigation
Certification
Deliver reliable machinery + shorten the time-to-market

## Slide 6
Cold temperatures influence materials, lubrication and performance of systems
 Some influences are difficult or time consuming to simulate
Notes: Extremely low temperature causes many fluids to congeal, which means that it cannot flow through mechanical systems efficiently. This fluid immobility can starve a pump, which causes potentially harmful vaporous cavitation in the system. This also results in high fluid and mechanical friction, as well as lubricant starvation for bearing surfaces.

## Slide 7
‘Offshore’ wind turbines
‘Hot climate’ wind turbines
‘Cold climate’ wind turbines
Some definitions with regard to low temperature climates to start with
‘standard’ wind turbines
Designed for
‘Survival’ temperature limit: -20°C to +50°C
‘Operational’ temperature limit: -10°C to +40°C
Design temperature standard wind turbine (avarage annual air temperature = +15°C)
Design limit for Low Temperature Climate (LTC) (structural endurance limit)
< -15°C: Operational limit for Low Temperature Climate (LTC) wind turbine
-10°C : Operational limit for standard wind turbines
Manufacturer defines the minimum ‘survival’ and minimum ‘operational’ temperature limit of the turbine
Source: Vestas
-30°C: Common operational limit for LTC
Notes: DNV –GL = certification guideline
Definition of cold climate site / conditions
• normal climate ambient temperatures:
• θmean year = 15°C
• θ1year min/max = -20 to +50°C (survival temperature)
• θmin/max operation = -10 to +40°C (operational temperature)
• standard air density ρ = 1.225kg/m3
• cold climate criterion and ambient temperatures:
• 9 days per year below -20°C (appr. p=0.02)
• operation of turbines below -15°C
• manufacturer defines θmean year , θ1year min , θmin operation

## Slide 8
‘Offshore’ wind turbines
‘Hot climate’ wind turbines
‘Cold climate’ wind turbines
Some definitions with regard to low temperature climates to start with
‘standard’ wind turbines
Designed for
‘Survival’ temperature limit: -20°C to +50°C
‘Operational’ temperature limit: -10°C to +40°C
Design temperature standard wind turbine (avarage annual air temperature = +15°C)
Design limit for Low Temperature Climate (LTC) (structural endurance limit)
< -15°C: Operational limit for Low Temperature Climate (LTC) wind turbine
-10°C : Operational limit for standard wind turbines
-30°C: Common operational limit for LTC
Notes: DNV-GL is only a certification guideline, not a standard. It will refer to certain standards.
IEC standard for wind turbines – under revision- takes into account the design loads and cold climate & low temperature are taken into account.
Component suppliers have their own standards on component level (for example gearbox or transformer) ; generic electro-technical standards also exist which apply to converters for example – solar converter = same technology as a wind turbine converter. Same for switch gears and switch cabinets etc….

## Slide 9
Largest "non standard" sectors for wind energy today !
Dedicated solutions and low temperature adaptations are developed to cope with the challenges of cold climates wind farms
Overview study of the ‘Available technology’ made by IEA Wind Task 19
Study made public recently – July 2016 (see website)
The study summarizes existing technologies and solutions from weather modelling, to ice detectors and turbine manufacturers that deal with wind energy in cold and icing conditions
Low temperature adaptations chapter included
http://www.ieawind.org/task_19.html
Recent article 29/07/2016: http://www.windpowermonthly.com/article/1403504/emerging-cold
Notes: Additional challenges for such sites:
Technology changes in design
Installation
Maintenance
Health & Safety

## Slide 10
Overview of most popular measures in “cold climate package”
MATERIALS: ‘Low temperature’ materials applied (special steel and cast iron alloys for structures ; elastomers) - gearbox, nacelle frame, hub, main shaft, bearing housing, seals, etc…
FLUIDS: ‘Low temperature’ oils & greases applied – gearbox, bearings, transformer, cooling, hydraulics,…
SPECIAL MEASURES: Anti & de-icing solutions, improved nacelle sealing, ice-detection sensors, dedicated cold start-up procedures (cold climate controller), foundation (water ingress)
Ice detection / no-ice detection
Blade de-icing:
Heating mats in composite
Hot air system
Gearbox:
Special materials
Special lubricants & grease
Additional (pre-) heating
Dedicated cold start-up procedures
Dedicated low temperature cooling fluids and cooling circuit
For gearbox, generator & converter
HEATING: Additional heaters added to switch cabinets and converters, gearboxes, hydraulics, anemometer, slip rings, nacelle space…
Ice detection
Heated anemometers

## Slide 11
Insights in field performance in low temperatures
Source: Azure international / Clean Energy – Winterwind 2016
Location wind farm: Mongolia (cold climate)
  Dry air conditions at this location in Mongolia – almost no influence of icing on power curve, only effect of the low temperatures
  Power loss due to:
    Cold weather shut-downs:
    The control system will shut the turbine down when the average temperature measured in the nacelle drops below -30°C.
    Cold weather de-rating:
    When T< -15°C and >-30°C the turbine will be operating below the optimal power curve. Reasons include oil heating and limiting stress forces

## Slide 12
Other industries: low temperatures in grid infrastructure
  Example of a 15MVA power transformer test campaign
  Test program at -40°C and -50°C for applications used in Canada, Russia, China, Mongolia and Scandinavia.
  The transformer is filled with environmentally friendly, but highly viscous synthetic ester fluid.
  High viscosity at low temperatures impedes natural fluid flow and thus leads to a change of thermal performance.
  Especially relevant in case of cooling by external radiators, which is standard for power transformers. Fluid flow in the small radiator ducts is completely different from flow at the tank wall, even more so in case of high viscosity.
  Results presented at:

## Slide 13
Lessons learned when testing wind turbine machinery
1.
2.
3.

## Slide 14
Liquid filled wind turbine transformers
  Risks during low temperatures:
    Under load – no risk due to transformer losses
    Stand-still in low temperature > 24h
        Risk of tank underpressure and related air suction due to shrinking of the transformer oil
        Risk of overpressure during cold start-up and warm-up in general as air can not evacuate fast enough
        Risk of accelerated temperature rise in windings as natural cooling convection is limited at low temperature (stiff fluids)
        Failure of auxiliaries and leakage (pumps, cooling circuits, radiators, tripping sensors, seals, etc.)
Poster and Paper available EWEA 2014: Cold start of a 5.5MVA offshore transformer

## Slide 15
Liquid filled wind turbine transformers
  Lessons learned during climate chamber tests:
    Design of the transformer tank flexibility should take low temperature cool down and start-up into account (under- and overpressure)
    Usage of correct type of pressure control in tank (hermetically sealed, gas cushion, breather, expansion tank)
    The importance of seals (eliminate air suction / leakage)
    Usage of the right auxiliaries that can work in cold climate
  Continuous optimization and R&D effort:
    New fatigue tank test bench – topic under & overpressure and effect on lifetime of transformer tank
    Field monitoring campaign of instrumented WTG transformer in cold climate

## Slide 16
Wind turbine gearboxes – cold start-up tests
  Risks during low temperatures:
    Ensure sufficient lubrication of gears and bearings during cold start-up procedure (CSP) as the oil is stiff.
    Cold-start-up time must be within a certain allowable time limit (based on customer requirements)
    Failure of auxiliaries and leakage (pumps, cooling circuits, filters, sensors, seals, etc.)  ensure survival limit of -40°C of all parts, even during a grid-disconnection.
    Ensure sufficient oil flow in pumps to mitigate risk of cavitation
    Heaters needed for pre-heating, but surface temperature of heaters should be low enough in order not to burn gearbox oil.
6.X MW
Cold-start-up test bench

## Slide 17
Wind turbine gearboxes – cold start-up tests
  General procedure (OEM / Supplier dependent):
  Lubrication oil is heated up in separate oil tank and the gearbox oil sump from -40°C to +10°C. Friction losses from gearbox are than used to heat-up the oil quicker, next rotor speed is increased in a pre-determined procedure until partial load and full load can be applied.
  Lessons learned during climate chamber tests:
    Generic lessons linked to the associated risks – example oil pumps, cavitation, seals,…
    Climate chamber test = Standard test in validation trajectory (Cf. Automotive or off-highway vehicle tests)
    Average cold-start-up time for gearbox: 5h – with wind
  Continuous optimization and R&D:
    Testing of new lubrication oils and their performance during cold-start

## Slide 18
Other components: pitch / yaw / brakes / converters
Statement DNV-GL note on Engineering Details: Wind Turbine operation down to –20°C
Requirements for certification: Evidence on safe operation of the main mechanical and electrical components. At least:
1. Components of the safety system and braking systems including the pitch system and the hydraulic system
2. Blade bearing, Main bearing (s)
3. Gearbox
4. Generator
5. Yaw bearing
6. Electrical Cabinets in Hub, Nacelle, Tower
7. Medium voltage switchgear and transformer
100kW
Time-to-market essential
Full scale test to proof cold climate compliance to customer
Cold start-up procedure (CSP) of pitch ; yaw and brake systems
Converter / generator test

## Slide 19
Contact person & more information
pieterjan.jordaens@owi-lab.be
be.linkedin.com/in/pieterjanjordaens/en
www.owi-lab.be
@OWI_lab
Knowledge sharing – LinkedIn Group: Offshore Wind Infrastructure Application Lab (OWI-Lab)